2021-07

ASSA ABLOY

OH1042FG Overhead sectional door

Tender Specification Text

# ASSA ABLOY OH1042FG Overhead sectional door

Product description

- Overhead sectional door/sectional door with panels of extruded, E6-EV1, anodized, high-strength aluminium profiles as supporting frame (Height 450 - 600 mm).

- Life time expectations door: 200.000 door cycles or 10 years, if service/replacement program is performed.

- Infills optionally single- or insulating glazing. One or two panes, depending on the daylight width of the door

- Integrated finger pinch protection

- Top, bottom and side seals and seals between door sections

- Standard track system in galvanized steel

- Spring balancing, 20.000 cycles

- Spring break device

- Lock bolt, step-handle,

- Compliance with all operational and safety instructions in EU Directives and the standards of the European Standardization Committee (CEN)

- Standard hardware (head room 485/510 mm to 800 mm)

- Operating system: manual

- Standard door sizes (DLW x DLH)
MIN: 2.050 x 2.150 mm
MAX: 5.500 x 4.250 mm

| - Resistance to wind load, EN12424 | Insulated panel sections | Class 3 (DLW ≤ 4250) Class 2 (4250 < DLW) (Higher classes on request) |
| --- | --- | --- |
|  | Framed sections | Class 3 (DLW ≤ 3650) Class 2 (3650 < DLW) (Higher classes on request) |
| - Thermal transmittance (EN 12428) | 6.0 W/(m²∙K) single glazing SH6 |  |
| - Water penetration (EN 12425) | Class 3 (Door 4.000 x 4.000 mm) |  |
| - Air permeability (EN 12426) | Class 3 (Door 4.000 x 4.000 mm) |  |

Glazing

- Standard: SH6 single glazing hardened glass

- Option: DH4D, double glazing 2 x 4 mm hardened glass

Thermal transmittance glazing, 2,75 W/(m²∙K)

- Option: DH6D, double glazing 2 x 6 mm hardened glass

Thermal transmittance glazing, 2,75 W/(m²∙K)

- Option: DE4D, double glazing 2 x 4 mm hardened glass with Argon filling

Thermal transmittance glazing, 1,1 W/(m²∙K)

- Option: DE6D, double glazing 2 x 6 mm hardened glass with Argon filling

Thermal transmittance glazing, 1,1 W/(m²∙K)

Bottom Sections

- Standard: Aluminium frame construction

- Option: Sandwich panel across entire width,

Section height 600 mm plus bottom seal

(other glazing / sandwich unit designs available on request)

Options

Surface color

- Aluminium frame

- Standard: E6/EV1 anodized

- Option: interior and / or exterior painted in standard colors

- Option: interior and / or exterior painted in RAL-standard color buyer’s choice

- Option: interior and / or exterior painted according to color sample

- Option: interior and exterior powder coated

- Sandwich panel

- Standard: Aluminium panel aluminium interior and exterior or

- Standard: Steel panel interior RAL 9002, exterior standard colors

- Option: Aluminium and steel panel interior and/or exterior painted according to color sample

- Option: Aluminium and steel panel interior and / or exterior painted in RAL-standard colors buyer’s choice

- Passdoor is not possible

Door locking device

- Option: Lock with profile cylinder lockable on one or both sides

- Option: Door locking switch (essential with electric operation)

Hardware

- LL	drop clearance, 265 mm (≤250 kg), 300 mm (>250 kg)

- HL	drop clearance, HL+320 mm (HL ≤3321 mm), HL+370 mm (HL >3321 mm)

- HHL	drop clearance, HL+220 mm (HL ≤3321 mm), HL+270 mm (HL >3321 mm)

VL	drop clearance min. door height + 400 mm

Operator

- Option: Chain hoist “T” (Gear ratio 1:4, Door weight max. 250 kg)

- Option: Chain hoist “U” (Gear ratio 1:3, Door weight over 250 kg)

- Option: Electronic operator:

- Operating voltage: 230 V AC, 50/60 HZ (internal supply 3-phase 230 V AC)

- Operating factor: ED = 30%, S3 10 min, non-continuous operation

- (Engine operation 3 min, pause 7 min, direct-inverting)

- Torque: 15-40 Nm, depending on reel type (value of given door shaft)

- Fusing: 10 A

- Brake: non-reversible worm gear

- Speed monitor: electronic monitoring

- Freewheel / clutch: mechanical engagement/disengagement

- Limit switch: electronic via torque (setting “Door open” during programming) Setting “Door closed” in processor board

- Gears: worm gear 1750 RPM yields approx. 24 rotations door shaft

- Shaft: ø35 mm or hexagonal

- Direct drive system

- No special wall reinforcement necessary

- Temperature range: -20°C to 60°C

- Soft stop, soft start

- Connection using “CEE plug” or lockable mains isolator

- Maximum door weight 400 kg

Options

- Chain transmission

- Chain guard

Other drive variants available on request subject to technical inspection

Control units

Control unit 950

Output 0.37 kW, input 1 x 230 V. Dimensions: 180 x 380 x 120 mm (wxhxd) including control unit with standard actuator UP-STOP-DOWN and pulse control incl. self-monitoring safety edge. Counter/error code display and servicing info display in top of control cabinet. Operating speed 0.25 m/s, safety rating IP 55. If there is a power failure, the disengage device enables manual operation at any time.

Options:

- Radio remote control

- “Open” (if open button is used during closing process - door immediately stops and opens completely)

- “Automatic close” (safety photo cell compulsory requirement) Door closes automatically after set period (4-60 sec)

- Pull switch for OPEN / CLOSE

- External push-button, key switch

- “One-button function” - opens or closes door, depending on actual status (e.g. radio, pull switch)

- additional safety (e.g. photo cell, radar) – door immediately opens completely

- D-Module (D1-D6)

- Photo cell

- Reduced opening height

- Radar

- Magnetic loop

- Warning lights

- Traffic lights

- Interlocking door function

- Door/bridge interlock

D-Module (automation module)

- D1 functions

- red lamps, inclusive, blinking continuously when door is moving

- red blinking light before “Automatic close”

- constant red light with door closed available

- Start time for blinking lights before closure can be set

- D3 - function incl.

- D2 functions

- Magnetic loop, inclusive, with various functions, e.g.

- “Safety and checkback signal”

- “Open and checkback signal”

- “Safety and open”

- “Open”

- A DIP switch can also be chosen to provide confirmation as additional safety

- D3 - function incl.

- D3 - functions

- Interlocking door function or mutual interlocking between two doors

- Door/bridge interlocking

- Incl. 24 V AC max. 400 mA for additional units

- Relay for “Door open” or “Door closed”

- D4 functions

- Combination of D1 and D2

- red lamps (inclusive) blinking continuously when door is moving

- red blinking light (inclusive) before “Automatic close”

- constant red light with door closed available

- Start time for blinking lights before closure can be set

- A DIP switch can also be chosen to provide confirmation as additional safety

- D3 - function incl.

- magnetic loop (inclusive) with various functions, e.g.

- “Safety and checkback signal”

- “Open and checkback signal”

- “Safety and open”

- “Open”

Note! Lights and position indications uses the two available outputs, combinations are limited, expansions/combinations on request.

- D5 functions

- Directional sensor traffic light (including red/green)

- Control of oncoming traffic in the doorway

- using “Open interior” or “Open exterior” to control oncoming traffic

- Oncoming traffic sees alternately red or green light, depending on which “Open command” is given first

- D3 - functions

- D6 functions

- Directional sensor traffic light with magnetic loop activation (inclusive), of “Open exterior”

- Control of oncoming traffic in the doorway

- using “Open interior” or “Open exterior” to control oncoming traffic

- Oncoming traffic sees alternately red or green light, depending on which “Open command” is given first

- D3 - functions

Other supplementary equipment

- Anti-corrosive hardware

- Anti-corrosive package Type “C”

- Stainless steel hinges and roller brackets

- Stainless steel screws

- Stainless steel roller shafts and door cables

- Aluminium top and bottom profile

- Powder coated corner bracket (RAL 9002)

- Anti- corrosive package Type “A”

- Stainless steel hinges and roller brackets

- Stainless steel screws

- Stainless steel roller shaft and door cables

- Aluminium top and bottom profile

- Powder coated corner bracket (RAL 9002)

- Powder coated end caps, trusses, tracks, hangers, connection beams, safety pull bracket (RAL 9002)

- Anti- corrosive package Type “S”

- Safety pull cables, stainless steel

- Anti- corrosive package Type “Z”

- Electro-galvanized springs (max. 70.000 cycles)

- Cable break device

- Increased cycle spring (20.000 – 100.000)

Special models

- Fixed top and side sections, with and without passdoor, in the same color and construction as the door leaf are available on request ! (subject to technical inspection)