SECTION 08 42 29.63 – SPECIAL FUNCTION SLIDING AUTOMATIC ENTRANCES

- GENERAL

  - SUMMARY

- NOTE:  Edit this specification as required for the project

- NOTE:  Size of the SL500 Windload R92 is as follows:

- Bi-Parting Entrance:		Maximum width	192”

- Single Slide Entrance	Maximum width	96”

- Frame Height			Maximum height	92” (as tested)

- Frame Height (Allowed)	Maximum height	96” (not tested)

    - This section includes the following types of automatic entrance doors:

      - Exterior wind resistant sliding automatic entrances subject to wind load pressures up to 55 PSF.

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - [Division 8 Section “Aluminum-Framed Entrances and Storefronts” for entrances furnished separately in Division 8 Section.]

      - [Division 8 Section “Door Hardware” for hardware to the extent not specified in this Section.]

      - Division 8 Section “Glazing” for materials and installation requirements of glazing for automatic entrance doors.

      - Division 26 and 28 Sections for electrical connections including conduit and wiring for automatic entrance door operators and access control devices.

  - REFERENCES

    - References:  Refer to the version year adopted by the Authority Having Jurisdiction.

      - ANSI A117.1 - Accessible and Usable Buildings and Facilities.

      - ICC/IBC - International Building Code.

      - NFPA 70 - National Electrical Code.

      - NFPA 101 - Life Safety Code.

    - American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA).

      - ANSI/BHMA A156.10 American National Standard for Power Operated Pedestrian Doors.

      - ANSI Z97.1 Standards for Safety Glazing Material Used in Buildings.

    - Underwriters Laboratories (UL).

      - UL 325 Standard for Safety for Door, Drapery, Gate, Louver and Window Operators and Systems.

    - American Association of Automatic Door Manufacturers (AAADM).

    - American Society for Testing and Materials (ASTM).

      - ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.

      - ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.

      - ASTM E283 – Standard Test Method for Determining the Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.

      - ASTM E330 – Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls, Doors by Uniform Static Air Pressure Difference. Testing conducted for both positive and negative pressure.

      - ASTM F842 – Standard Test Methods for Measuring the Forced Entry Resistance of Sliding Door Assemblies, Excluding Glazing Impact.

    - American Architectural Manufacturers Association (AAMA).

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

      - AAMA 1304 Voluntary Specification for Determining Forced Entry Resistance of Side-Hinged Door Systems.

    - National Association of Architectural Metal Manufacturers (NAAMM).

      - Metal Finishes Manual for Architectural Metal Products.

    - International Code Council (ICC).

      - [IBC:  International Building Code Building Code.]

      - [CBC: California Building Code.]

- NOTE:  The following requires the U-Factor Glazing specified in this specification – Delete if not needed for project

    - [National Fenestration Rating Council (NFRC).]

      - ANSI/NFRC 100-2020:  Procedure for Determining Fenestration Product U-Factors.

      - ANSI/NFRC 200-2020:  Procedure for Determining Fenestration Product Solar Heat Gain Coefficient and Visible Transmittance at Normal Incidence.

      - ANSI/NFRC 500-2020:  Procedure for Determining Fenestration Product Condensation Resistance Values.

    - [ASHRAE 90.1-2019: Energy Standard for Buildings Except Low-Rise Residential Buildings.]

  - DEFINITIONS

    - Activation Device: Device that, when actuated, sends an electrical signal to the door operator to activate the operation of the door.

      - Knowing act:	Consciously initiating the opening of a power operated door using acceptable methods including wall mounted switches such as push plates and controlled access devices such as keypads, card readers and key switches.

    - Safety Device: A device that detects the presence of an object or person within a zone where contact could occur and provides a signal to stop the movement of the door.

  - PERFORMANCE REQUIREMENTS

    - Compliance with the following:

      - ANSI/BHMA A156.10 American National Standard for Power Operated Pedestrian Doors.

      - UL 325 listed.

    - Automatic door equipment accommodates medium to heavy pedestrian traffic.

    - Entrapment Force Requirements:

      - Power Operated Sliding Doors: Not more than 30 lbf (133 N) required to prevent stopped door from closing.

      - Sliding doors provided with a breakaway device shall require no more than 50 lbf (222N) applied 1 inch (25 mm) from the leading edge of the lock stile for the breakout panel to open.

    - Forced Entry Requirements:  Sliding automatic entrances shall have been evaluated by an accredited laboratory for forced entry resistance per ASTM F842 – Standard Test Methods for Measuring the Forced Entry Resistance of Sliding Door Assemblies, Excluding Glazing Impact.

      - Must pass Grade 10 with No Entry.

- NOTE:  Delete the following if not required for the project

    - [ASTM E283-2019:  Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.]

- NOTE:  The following requires the U-Factor Glazing specified in this specification – Delete if not needed for project

    - [Energy Code Requirements:  Sliding automatic entrances that are required to meet construction energy code requirements shall have been evaluated based on methodology in accordance with the following National Fenestration Rating Council (NFRC) standards:]

      - ANSI/NFRC 100-2020:  Procedure for Determining Fenestration Product U-Factors.

      - ANSI/NFRC 200-2020:  Procedure for Determining Fenestration Product Solar Heat Gain Coefficient and Visible Transmittance at Normal Incidence.

      - ANSI/NFRC 500-2020:  Procedure for Determining Fenestration Product Condensation Resistance Values.

  - SUBMITTALS

    - Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.

    - Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, and fabrication of doors, frames, sidelites, operator, motion /presence sensor control device, anchors, hardware, finish, options and accessories.

    - Samples: Submit manufacturer’s samples of aluminum finish.

    - Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification.

      - Credit MR 4: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

    - Test Reports:  Submit certified test reports indicating doors comply with specified performance requirements.

    - Actual Wind Load Pressure Performance Report:  Submit sealed reports from a licensed structural engineer indicating the actual wind load performance of the sliding automatic entrance.

    - Forced Entry Reports:  Submit certified test reports from an accredited laboratory indicating passing “Grade 10 with No Entry” requirements for forced entry resistance per ASTM F842 – Standard Test Methods for Measuring the Forced Entry Resistance of Sliding Door Assemblies, Excluding Glazing Impact.

    - Manufacturers Field Reports:  Submit manufacturer’s field reports from AAADM certified technician of inspection and approval of doors for compliance with ANSI/BHMA A156.10 after completion of installation.

- NOTE:  Delete the following if not required for the project

    - [Air Infiltration Performance:  Submit test reports showing actual air infiltration when tested per ASTM E283-2019.]

- NOTE:  The following requires the U-Factor Glazing specified in this specification – Delete if not needed for project

    - [Energy Calculations:  Submit computer simulation data that is based on methodology in accordance with the National Fenestration Rating Council (NFRC) standards: ANSI/NFRC 100-2020, ANSI/NFRC 200-2020, ANSI/NFRC 500-2020.]

    - Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the complete door opening installation in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the hardware and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.

    - Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.

  - QUALITY ASSURANCE

    - Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.  Manufacturer to have a company certificate issued by AAADM.

    - Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum 3 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

    - Certified Inspector Qualifications: Certified by AAADM.

    - Source Limitations for Automatic Entrances:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.

    - Power-Operated Pedestrian Door Standard: ANSI/BHMA A156.10 (current version).

    - Emergency Exit door requirements: Comply with requirements of authorities having jurisdiction for automatic entrance doors serving as a required means of egress.

  - PROJECT CONDITIONS

    - Field Measurements:  Verify actual dimensions of openings to receive automatic entrances by field measurements before fabrication and indicate on shop drawings.

  - COORDINATION

    - Coordinate sizes and locations of recesses in concrete floors for recessed tracks and thresholds if applicable. Concrete work is specified in Division 03.

    - Electrical System Roughing-in: Coordinate layout and installation of automatic entrances with connections to power supplies and access control system as applicable.

  - WARRANTY

    - General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

    - Automatic Entrance Doors shall be free of defects in material and workmanship for a period of One (1) year from the date of substantial completion.

    - During the warranty period a factory-trained technician shall perform service and affect repairs. An inspection shall be performed after each adjustment or repair.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.

    - Manufacturer shall have in place a dispatch procedure that shall be available 24 hours a Day, 7 Days a week for emergency call back service.

- PRODUCTS

  - MANUFACTURER

    - Manufacturer:  ASSA ABLOY Entrance Systems, 1900 Airport Road, Monroe, NC 28110. Toll Free (877) SPEC-123.  Fax (704 ) 290- 5555 Website: www.assaabloyentrance.us  contact:  specdesk.na.entrance@assaabloy.com

- NOTE:  Revise the following substitution clause as required by project requirements.

- Select either Item “B” or “C”

    - [Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

    - [Substitutions:  Not Permitted.]

  - SLIDING AUTOMATIC ENTRANCES

    - Sliding automatic entrance system including the following:

      - Sliding panels, sidelites and aluminum frame.

      - Overhead concealed, electro-mechanical operator.

      - Operator housing, guide system and carrier assemblies.

      - Controls and accessories as required for a complete installation.

    - Performance Requirements:

- NOTE:  The following requires the E283 Door Seals specified in this specification – Delete if not required for the project

      - [Air Infiltration per ASTM E283 – Standard Test Method for Determining the Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.]

        - Maximum air leakage of 1.0 cfm/ft2 at 1.57 psf (25 mph).

      - Structural Performance (wind load) tested according to requirements of TAS 202, ASTM E330 – Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls, Doors by Uniform Static Air Pressure Difference. Testing conducted for both positive and negative pressure.

- NOTE:  The minimum pressure listed below is the actual pressure achieved based on physical testing of the maximum entrance frame size as listed

        - Minimum actual wind load pressure not less than 55 PSF.  (Performance is based on a 92-inch frame height x 192-inch frame width.)

          - No more than 0.368” of permanent set will be acceptable.

          - Performance shall be verifiable by a test report sealed by a licensed structural engineer.

      - Forced Entry Resistance per FBC TAS 202, ASTM F842 – Standard Test Methods for Measuring the Forced Entry Resistance of Sliding Door Assemblies, Excluding Glazing Impact.

        - Must pass Grade 10 with No Entry.

- NOTE:  The following requires the U-Factor Glazing specified in this specification – Delete if not needed for project

      - [Thermal Performance – Door assembly shall have been evaluated in full compliance with the listed National Fenestration Rating Council (NFRC) standards: ANSI/NFRC 100-2020, ANSI/NFRC 200-2020, ANSI/NFRC 500-2020.]

        - The U-factor rating of the entrance, as well as the solar heat gain coefficient, visible light transmittance condensation resistance, and emissivity is dependent on the glazing specified.  See glass specifications.

- NOTE:    Select entrance configuration(s) as required for the project

    - ASSA ABLOY SL500 Windload R92 Automatic Sliding Entrance (Basis of Design) with Stile and Rail Panels:

      - [Wind resistant, single slide, full breakout, door system.]

        - Configuration:  Single slide, two equal panel unit with one operable leaf and one sidelite.

        - Traffic Pattern:  [Two-way.]  [One-way.]

        - Emergency Breakaway Capability:  Sliding leaf and sidelite.

        - Mounting:  Overhead header installed between jambs.

      - [Wind resistant, single slide, fixed sidelite, door system.]

        - Configuration:  Single slide, two equal panel unit with one operable leaf and one fixed sidelite.

        - Traffic Pattern:  [Two-way.]  [One-way.]

        - Emergency Breakaway Capability:  Sliding leaf only.

        - Mounting:  Overhead header installed between jambs.

      - [Wind resistant, bi-parting, full breakout, door system.]

        - Configuration:  Bi-parting, four equal panel unit with two operable leaves and two sidelites.

        - Traffic Pattern:  [Two-way.]  [One-way.]

        - Emergency Breakaway Capability:  Sliding leaves and sidelites.

        - Mounting:  Overhead header installed between jambs.

      - [Wind resistant, bi-parting, fixed sidelite, door system.]

        - Configuration:  Bi-parting, four equal panel unit with two operable leaves and two fixed sidelites.

        - Traffic Pattern:  [Two-way.]  [One-way.]

        - Emergency Breakaway Capability:  Sliding leaves only.

        - Mounting:  Overhead header installed between jambs.

  - ENTRANCE COMPONENTS

    - Stile and Rail Sliding Panels and Sidelites:

      - Material:  Extruded Aluminum, Alloy 6063-T5.

      - Door panels shall have a minimum .125 inch (3.2 mm) structural wall thickness including adjoining horizontal members and perimeter frames where applicable.

      - Door construction shall be by means of self-aligning aluminum clips with 3/8 inch all-thread through bolt from each stile.

      - Glass stops shall be 0.090” (2.79mm) wall thickness.

      - Full breakout sliding entrances shall include two interlocks per moving panel securing the leading stile of the sidelite and the butt stile of the sliding door panel together.

        - Interlocks to be automatic engaging and releasing during open-close cycles.

- NOTE:  U-Factor of the entrance assembly is affected by the door stile width – a narrow stile door provides a better U-Factor

- NOTE:  Thermal performance ratings (U-factor, solar heat gain coefficient, visible light transmittance, condensation resistance, and emissivity ratings) are not available for entrances with medium stiles

      - Vertical Stiles shall be [narrow stile 2-1/8 inch (54 mm).]  [medium stile 4 inch (102 mm).]

      - Bottom Rails shall be [4 inch (102 mm).]  [7 inch (178 mm).]  [10 inch (254 mm).]

      - [Intermediate Muntin shall be [1-3/4 inch (45 mm).]  [4 inch (102 mm).]

      - Weather-Stripping:  Slide-in type, replaceable pile mohair seals retained by the aluminum extrusions.  The following types of weather-stripping are required:  complementing weather-stripping on the joining vertical stiles of the sidelite and sliding door panels, complementing weather-stripping on the lead edge of the lock stiles of bi-parting doors, single pile weather-stripping between the carrier and the header, single pile weather-stripping on the lead edge stile of single slide door panels, dual pile weather-stripping on the pivot stile of breakout sidelite panels, and dual pile weather-stripping on the butt stile of fixed sidelite panels.  Bottom rails shall be provided with an adjustable nylon sweep.

- NOTE:  Retain the following “E283 Door Seals” if obtaining the maximum air leakage of 1.0 cfm/ft2 at 1.57 psf per ASTM E283 is required

        - [E283 Door Seals:  High pile mohair weather stripping on the lock stile of the sliding doors, mohair weather stripping on the joining vertical stiles of the sidelite and sliding door panels, and expandable foam inserts in leading stile of sidelite panels at pockets for interlocks.  Bottom rails shall be provided with dual concealed adjustable nylon sweeps.]

- NOTE:  Select from the following glazing types for the project.  Add “Locations” to each of the following if multiple types and/or thickness glazing are required

      - Glass:  Glazing shall comply with ANSI Z97.1, thickness as indicated.

        - [Glazing – Wind Resistant Entrances:  1/4” (6 mm) tempered glass.]

        - [Laminated Glazing – Wind Resistant Entrances:  9/16” overall thickness, laminated glass consisting of an approved interlayer laminated between two pieces of 1/4 inch (6mm) heat strengthened glass panes.]

          - Approved Interlayers:

            - [.030” PVB.]

            - [.060” PVB.]

        - [Laminated Impact Glazing – Wind Resistant Entrances:  9/16” overall thickness, laminated glass consisting of an approved interlayer laminated between two pieces of 1/4 inch (6mm) heat strengthened glass panes.]

          - Approved Interlayers:

            - .090” SentryGlas Plus® by DuPont.

        - [Insulated Glazing – Wind Resistant Entrances:  1” (25 mm) insulated glass with 1/4” tempered panes.]

        - [U-Factor Laminated Impact Glazing – Wind Resistant Entrances:  9/16” overall thickness, laminated glass consisting of an approved interlayer laminated between two pieces of 1/4 inch (6mm) heat strengthened glass panes.]

          - Approved Interlayers:

            - Solarban 60(E) – .090 SGP SentryGlas Plus.

- NOTE:  The following values are based on a SL500 Windload R92 narrow stile entrance, glazed with PPG Solarban 60(E) Clear

          - Glazing shall be PPG Solarban 60(E).  The sliding automatic entrance assembly with narrow stiles shall meet the following requirements:

            - U-Factor Rating			1.04 BTU/(h oF ft2)

            - Solar Heat Gain Coefficient 	0.312

            - Visible Light Transmittance	0.440

            - Condensation Resistance		17

            - Emissivity				0.035 (embedded)

        - [U-Factor Insulated Glazing – Wind Resistant Entrances:  1” (25 mm) overall thickness insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) clear tempered glass  Airspace to be 90% argon filled.]

- NOTE:  The U-factor rating of the entrance, as well as the solar heat gain coefficient, visible light transmittance condensation resistance, and emissivity is dependent on the glazing specified.

- NOTE:  The following values are based on a SL500 Windload R92 narrow stile entrance, glazed with PPG Solarban 60 Clear, coated on surface 2, and the airspace 90% argon filled.  Consult with the SpecDesk for values of entrances with other types of glazing including PPG Solarban 70, Cardinal LoE-270, Guardian ClimaGuard 70/36, Guardian Sunguard SuperNeutral 68, Guardian Sunguard SNX 62, AGC Energy Select 40, AGC Energy Advantage

- NOTE:  Thermal performance ratings (U-factor, solar heat gain coefficient, visible light transmittance, condensation resistance, and emissivity ratings) are not available for entrances with medium stiles

          - Glazing shall be [PPG Solarban 60 Clear, coated on surface 2, and the airspace 90% argon filled.]  The sliding automatic entrance assembly with narrow stiles shall meet the following requirements:

            - U-Factor Rating			[0.64 BTU/(h oF ft2)]

            - Solar Heat Gain Coefficient 	[0.271]

            - Visible Light Transmittance	[0.436]

            - Condensation Resistance		[20]

            - Emissivity				[0.035]

        - Glazing Installation:  Refer to the sliding entrance manufacturer instructions to meet the specified performance of the sliding entrance.

          - [All Glazing furnished “by others”.]

          - Door panels must be dry glazed using a captive seal and press-in wedge seal.

            - Glazing installation with silicone sealant is not acceptable.

          - No exposed fasteners in the glazing stops will be acceptable.

    - Door Carriers:  Manufacturer’s standard carrier assembly that allows vertical adjustment.

      - Carriage Assembly:  Carriage bar with two wheel assemblies.  Each assembly shall have tandem roller wheels.

      - Roller Wheels:  Two heavy duty Delrin roller wheels per wheel assembly, for a total of four (4) roller wheels, 1-7/16 inch (36.51 mm) diameter, per active door leaf for operation over a replaceable aluminum track. Single journal with sealed oil impregnated bearings.

      - Two (2) heavy duty self-aligning anti-risers per leaf.

    - Framing Members:  Provide automatic entrances as complete assemblies.  Manufacturer’s standard extruded aluminum framing reinforced as required to support loads.

      - Sliding Entrance - Vertical Jambs:  1-3/4 inches (44.5 mm) by 4-1/2 inches (114.3 mm).

    - Header:  Manufacturer’s standard extruded aluminum header with a replaceable aluminum track extending full width of entrance unit.  Header to conceal door operators, carrier assemblies, and roller track; complete with hinged access panel for service of door operator, and controls.

- NOTE:  Consult SpecDesk for oversized packages

      - Header Span:   Maximum 16’-0” (4.9 m) without intermediate supports when entrance glazed with 1/4-inch glass.

        - Capacity:  Capable of supporting active breakout leafs up to maximum of 300 lb (136 kg) per leaf when header is supported per manufacturer’s recommendations.

      - Header Size:  4-1/2 inches (114.3 mm) wide by 7 inches (177.8 mm) high.

        - Header height including the sensor plate cap which spans the clear door opening width is 8 inches (203.2 mm) high.

      - Header Access:  Continuous hinge at top of header allows cover to swing and allow complete access to operator and internal electronic and mechanical assemblies.

      - Design:  Closed header when doors in closed position.

  - HARDWARE

    - Hardware:  Provide manufacturer’s standard hardware as required for operation indicated.

      - Breakaway arms and bottom pivot assemblies shall be supplied by the manufacturer and shall be adjustable to comply with applicable codes.

- NOTE:  The optional dampers control the doors in the breakout function

      - [Wind resistant hydraulic 90 degree damper to control movement of breakout panels.]

      - [Concealed mounted friction bar with adjustable resistance to control movement of the breakout panel to the 90 degree stop position.]

      - [Bottom ball detent on breakout sidelite panels to provide additional wind resistance.]

- NOTE:  Consult SpecDesk for locking hardware options and hardware for access control

- NOTE:  If exit devices are required for emergency egress on secured entrances, retain the electrified slide lock option to lock the sliding function of the entrance

      - Locking hardware shall be provided as indicated.

        - [Electrified slide lock shall automatically lock the sliding function of all sliding door panels within the entrance when the door panels are in the closed position.]

          - [Fail secure operation:  Slide lock shall lock the sliding function of the door panels upon loss of power.]

          - [Fail safe operation:  Slide lock shall unlock the sliding function of the door panels upon loss of power.]

          - Exterior jamb mounted key switch to unlock sliding door operation.

- NOTE:  The following manual locking system is required for single slide entrances

        - [Three point locking system on each active leaf with hookbolt latch and throw rod/solid steel bolts into carrier arm and into threshold.]

          - Locking System:  Locking shall not require more than one operation for release of each active panel.

- NOTE:  The Adams Rite 4550 lever is not available on the fixed sidelite entrances

          - Interior Side: [Thumbturn.]  [Keyed cylinder.]  [Adams-Rite 4550 lever.]

            - Lock indicators shall be provided.

          - Exterior Side: [Keyed cylinder.]  [No cylinder.]

- NOTE:  The following manual locking system is required for bi-parting entrances

        - [Two point locking system on each active leaf with throw rod/solid steel bolts into carrier arm and into threshold.]

          - Locking System:  Locking shall not require more than one operation for release of each active panel.

- NOTE:  The Adams Rite 4550 lever is not available on the fixed sidelite entrances

          - Interior Side: [Thumbturn.]  [Keyed cylinder.]  [Adams-Rite 4550 lever.]

            - Lock indicators shall be provided.

          - Exterior Side: [Keyed cylinder.]  [No cylinder.]

- NOTE:  Exit devices allow the breakout function to be secure from the exterior side while still allowing emergency egress

- NOTE:  The exit device is not available on the fixed sidelite entrances

        - [Exit devices shall lock the breakout function while allowing emergency egress at all times.  Exit devices in combination with the automatic slide locking hardware to be provided on secured doors.]

- NOTE:  Surface mounted exit devices are only available with the full breakout entrance

          - Adams-Rite G86 concealed vertical rod exit device with throw rod into carrier arm and into threshold; mounted to active doors (full breakout entrances only).  Exit devices have hex key dogging.

      - Keyed cylinders shall be provided as indicated.

        - [Manufacturer’s standard keyed cylinder.]

        - [Keyed cylinder specified in Division 8 Section “Door Hardware”.]

        - [Keyed cylinder by others.]

    - Guide Track/Threshold:  Manufacturer’s threshold as indicated.

- NOTE:  The following is the required threshold/track for full breakout entrances

      - [Full Breakout Entrance Threshold:  1/2 inch (12.7 mm) high continuous aluminum threshold with integral track shall span the width of the sliding door header and fit between the vertical framing members.  Threshold design shall allow for optional extruded ramps to securely interlock to flat section to meet ADA requirements.]

        - [Surface mounted threshold with interlocking ADA accessible ramps.]  [Recessed mounted threshold.]

- NOTE:  The following is the required threshold/track for fixed sidelite entrances

      - [Fixed Sidelite Entrance Threshold:  1/2 inch (12.7 mm) high continuous aluminum threshold shall span the width of the sliding door header and fit between the vertical framing members.  Threshold design shall allow for optional extruded ramps to securely interlock to flat section to meet ADA requirements.  Aluminum guide track is integrated into the bottom of the sidelite portion of the door assembly.]

        - [Surface mounted threshold with interlocking ADA accessible ramps.]  [Recessed mounted threshold.]

  - DOOR OPERATORS AND CONTROLS

    - Door Operator and Controller:

      - Electro-mechanical controlled unit utilizing a high-efficiency, energy efficient, DC motor requiring a maximum of 3 amp current draw, allowing 5 operators on one 20 amp circuit. The supplied system shall have the capability to operate at full performance well beyond a brown out and high line voltage conditions (85V – 265V) sensing changes and adjusting automatically.  The operator shall allow an adjustable hold open time delay of 0 to 60 seconds and have internal software to incorporate a self-diagnostic system.

        - Operating Temperature Range: -31 F to 130 F (-35 C to 54.44 C).

    - Microprocessor Control Box:

      - Modular control unit to allow for changing technology.  Factory-adjusted configuration with opening and closing speeds set to comply with ANSI/BHMA A156.10 requirements and electronic dampening to reduce wear on drive train. Should the drive train operations deviate from design criteria ranges, Watchdog Control Circuit Monitoring will assume command of the system and shut down the automatic function allowing a secondary supervisory circuit to perform as a backup.  Control unit shall allow the following functions:

        - Diagnostics with the ability to produce application data.

      - Mode Selector Control:

- NOTE:  The standard mode selector control is the rotary knob switch

        - Multi-position [rotary knob] [keyed cylinder] mode selector control shall allow selection of the indicated functions to be engaged when switch is turned to the appropriate setting.

- NOTE:  The standard mounting location is jamb mounted

        - Mode Selector Control Mounting:  Control shall be mounted as indicated:

          - [Jamb mounted.]

          - [Remote mounted.]

        - Mode selector control to allow the following functions:

          - “Off”

          - “Exit Only” one way traffic with automatic operation from the interior.

          - “Two Way Traffic” allowing automatic operation from exterior and interior.

          - “Partial Opening” energy saving door position allows door to only open partially upon activation from exterior and interior.

          - “Hold Open” doors activated and held in the full open position.

  - ACTIVATION AND SAFETY CONTROL DEVICES

    - General:  Provide the types of activation and safety devices specified in accordance with ANSI/BHMA standards, for the condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate activation and safety devices with door operation and door operator mechanisms.

    - Combination Activation Motion Sensor/Safety Presence Sensor:

      - Shall be a sliding door sensor utilizing K-band microwave technology to detect motion and focused active infrared technology to detect presence, combined in a single housing surface mounted on each side of the header.

        - Presence sensor shall remain active at all times.

        - The sensor shall communicate with the automatic door operator through a self-monitoring connection that allows the door to go into a fail-safe mode preventing the door from closing in the event of a sensor failure.

      - Motion/presence detecting sensors to be field installed and adjusted.

- NOTE:  Cotact SpecDesk for “Knowing Act Activation” device options.  Ex: push plates

  - ELECTRICAL

    - High-Efficiency DC Motor: Maximum of 3 amp current draw, allowing 5 operators to run on one 20 Amp circuit.

    - Power:  Self-detecting line voltage capable control. 120 VAC through 240 VAC, 50/60 Hz, 3 amp minimum incoming power with solid earth ground connection for each door system.

    - Wiring:  Separate internal channel raceway free from moving parts.

    - Brown out / high voltage capability: System has capability to operate at full performance well beyond brown out and high voltage line conditions (85 V – 265 V) sensing changes and adjusting automatically.

    - [Convenience Battery: Shall be concealed in header and capable of full operation with blackout conditions, including sensor capabilities for minimum of 100 cycles.]

    - [Digital Cycle Counter:  Battery powered, 7 digit LCD cycle counter with a reset feature to track door usage cycles.]

  - ALUMINUM FINISHES

- NOTE:  Consult SpecDesk for custom finish options

    - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

    - [Anodized Finish:]

      - [AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

      - [AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

      - [AAMA 611, Custom anodized to match architect’s sample.]

    - [Painted Finish:]

      - [Powder coat painted to match architect’s sample.]

      - [Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

    - [To match architects sample.]

- EXECUTION

  - EXAMINATION

    - Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance.

    - Examine roughing-in for electrical source power to verify actual locations of wiring connections.

    - Proceed only after such discrepancies or conflicts have been resolved.

  - INSTALLATION

    - Do not install damaged components.  Fit frame joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Entrances:  Install automatic entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

      - Install surface mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, carrier assemblies, tracks, operating brackets and guides level and true to location with anchorage for permanent support.

        - Install entrance with a maximum 1/4" shim space as required by state and local hurricane product approvals.

    - Door Operators:  Connect door operators to electrical power distribution system as specified in Division 26 Sections.

    - Glazing:  Glaze sliding automatic entrance in accordance with the Glass Association of North America (GANA) Glazing Manual, published recommendations of glass product manufacturer, and published instructions of automatic entrance system manufacturer.

    - Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to provide a weather tight installation.

      - Set thresholds, bottom guide and track systems and framing members in full bed of sealant.

      - Seal perimeter of framing members with sealant.

    - Signage:  Apply signage on both sides of each door and sidelite as required by ANSI/BHMA A156.10 and manufacturers installation instructions.

  - ADJUSTING

    - Adjust door operators, controls and hardware for smooth and safe operation and for weather tight closure. Adjust doors in compliance with ANSI/BHMA A156.10.

  - FIELD QUALITY CONTROL

    - Before placing doors into operation, AAADM certified technician shall inspect and approve doors for compliance with ANSI/BHMA A156.10. Certified technician shall be approved by the manufacturer.

  - CLEANING AND PROTECTION

    - Clean adjacent surfaces soiled by door installation.

    - Clean glass and metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages to match original finish.

  - DEMONSTRATION

    - Engage a factory-authorized representative to train Owner's maintenance personnel to adjust, operate, and maintain safe operation of the door.

END OF SECTION