SECTION 08 42 29.33 – SWINGING AUTOMATIC ENTRANCES

- GENERAL

  - SUMMARY

- NOTE:  Edit this specification as required for the project

    - This section includes the following types of automatic entrance doors:

      - Exterior and interior swinging automatic entrances.

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - [Division 8 Section “Aluminum-Framed Entrances and Storefronts” for entrances furnished separately in Division 8 Section.]

      - [Division 8 Section “Sliding Automatic Entrances” for single and bi-parting sliding automatic entrance doors with sidelites.]

      - [Division 8 Section “Door Hardware” for hardware to the extent not specified in this Section.]

      - Division 8 Section “Glazing” for materials and installation requirements of glazing for automatic entrance doors.

      - Division 26 and 28 Sections for electrical connections including conduit and wiring for automatic entrance door operators and access control devices.

  - REFERENCES

    - References:  Refer to the version year adopted by the Authority Having Jurisdiction.

      - ANSI A117.1 - Accessible and Usable Buildings and Facilities.

      - ICC/IBC - International Building Code.

      - CUL – Approved for use in Canada.

      - NFPA 70 - National Electrical Code.

      - NFPA 101 - Life Safety Code.

    - American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA).

      - ANSI/BHMA A156.10 American National Standard for Power Operated Pedestrian Doors.

      - ANSI Z97.1 Standards for Safety Glazing Material Used in Buildings.

    - Underwriters Laboratories (UL).

      - UL 325 Standard for Safety for Door, Drapery, Gate, Louver and Window Operators and Systems.

      - UL991 Listed - Tests for Safety-Related Controls Employing Solid-State Device.

      - UL244A – Solid – State Controls for Appliances.

      - UL1998 – Software in Programmable Components.

      - UL1310 – Class 2 Power Units.

    - [Canadian Standards Association (CSA).

      - CAN/CSA-C22.2 NO 223-M91 –  Power Supplies With Extra-Low-Voltage Class 2 Outputs.

      - CAN/CSA-C22.2 No. 223-M92 – Operators and Systems of Doors, Gates, Draperies, and Louvers.]

    - American Association of Automatic Door Manufacturers (AAADM).

    - American Society for Testing and Materials (ASTM).

      - ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.

      - ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.

    - American Architectural Manufacturers Association (AAMA).

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

    - National Association of Architectural Metal Manufacturers (NAAMM).

      - Metal Finishes Manual for Architectural Metal Products.

    - International Code Council (ICC).

      - [IBC:  International Building Code.]

      - [CBC: California Building Code.]

  - DEFINITIONS

    - Activation Device: Device that, when actuated, sends an electrical signal to the door operator to activate the operation of the door.

      - Knowing act:	Consciously initiating the opening of a power operated door using acceptable methods including wall mounted switches such as push plates and controlled access devices such as keypads, card readers and key switches.

    - Safety Device: A device that detects the presence of an object or person within a zone where contact could occur and provides a signal to stop the movement of the door.

  - PERFORMANCE REQUIREMENTS

    - Compliance with the following:

      - ANSI/BHMA A156.10 American National Standard for Power Operated Pedestrian Doors.

    - Automatic door equipment accommodates medium to heavy pedestrian traffic.

    - Opening Force requirements for Egress Doors: In the event of power failure to the operator, swinging automatic entrance doors shall open with a manual force, not to exceed 30lbf (133N) applied at 1” (25 mm) from the latch edge of the door.

    - Break Away Device:  Swinging automatic entrances shall require no more than 50 lbf (222 N) applied 1” (25 mm) from the latch edge of the door.  When the door(s) is opened in the breakout mode, powered operated components excluding spring power shall not operate the doors.

    - Closing Time:

      - Doors shall be field adjustable to close from 90 degrees to 10 degrees in 2 seconds or longer as applicable per ANSI/BHMA A156.10 standards.

      - Doors shall be field adjusted to close from 10 degrees to fully closed in not less than 1.5 seconds.

  - SUBMITTALS

    - Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.

    - Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, operator, motion /presence sensor control device, anchors, hardware, finish, options and accessories.

      - Indicate required clearances, and location and size of each field connection.

      - Indicate locations and elevations of entrances showing activation and safety devices.

      - Wiring Diagrams:  For power, signal, and activation / safety device wiring.

    - Samples: Submit manufacturer’s samples of aluminum finish.

    - Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification.

      - Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

    - Manufacturers Field Reports:  Submit manufacturer’s field reports from AAADM certified technician of inspection and approval of doors for compliance with ANSI/BHMA A156.10 after completion of installation.

    - Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the complete door opening installation in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the entrance and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.

    - Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.

  - QUALITY ASSURANCE

    - Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.  Manufacturer to have a company certificate issued by AAADM.

    - Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum 3 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

    - Certified Inspector Qualifications: Certified by AAADM.

    - Source Limitations for Automatic Entrances:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.

    - Certifications: Operators shall be certified by the manufacturer to meet performance design criteria in accordance with the following standards.

      - ANSI/BHMA A156.10 American National Standard for Power Operated Pedestrian Doors.

      - UL 325 - Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

    - Emergency Exit door requirements: Comply with requirements of authorities having jurisdiction for automatic entrance doors serving as a required means of egress.

  - PROJECT CONDITIONS

    - Field Measurements:  Verify actual dimensions of openings to receive automatic entrances by field measurements before fabrication and indicate on shop drawings.

  - COORDINATION

    - Coordinate sizes and locations of recesses in concrete floors for recessed tracks and thresholds if applicable. Concrete work is specified in Division 03.

    - Electrical System Roughing-in: Coordinate layout and installation of automatic entrances with connections to power supplies and access control system as applicable.

  - WARRANTY

    - General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

    - Automatic Entrance Doors shall be free of defects in material and workmanship for a period of One (1) year from the date of substantial completion.

    - During the warranty period a factory-trained technician shall perform service and affect repairs. An inspection shall be performed after each adjustment or repair.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.

    - Manufacturer shall have in place a dispatch procedure that shall be available 24 hours a Day, 7 Days a week for emergency call back service.

- PRODUCTS

  - MANUFACTURER

    - Manufacturer:  ASSA ABLOY Entrance Systems, 1900 Airport Road, Monroe, NC 28110. Toll Free (877) SPEC-123.  Fax (704 ) 290- 5555 Website www.assaabloyentrance.com contact: specdesk.na.aaes@assaabloy.com

- NOTE:  Revise the following substitution clause as required by project requirements.  Select either Item “B” or “C”

    - [Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

    - [Substitutions:  Not Permitted.]

  - SWINGING AUTOMATIC ENTRANCES

    - Swinging automatic entrance system including the following:

      - Swinging door and aluminum frame with optional transom panel.

      - Overhead mounted, electro-mechanical, microprocessor controlled, swinging door operator.

      - Controls and accessories as required for a complete installation.

    - Besam ASSA ABLOY SW200i with Door Package swinging automatic entrance with sensor system. (Basis of Design):

      - Door Configuration:  Automatic operated swing door(s); configuration(s) and size(s) as indicated on the drawings.

        - Single Swing Door:  One active leaf (primary panel).

        - Pair of Swing Doors:  Two simultaneous swing, active leaves (both primary panels).

        - Double Egress Swing Doors:  Two simultaneous swing, active leaves (both primary panels) swinging in opposite directions.

        - Traffic Pattern:  [Two-way.]  [One-way.]

  - ENTRANCE COMPONENTS

    - Stile and Rail Swinging Doors:

      - Material:  Extruded Aluminum, Alloy 6063-T5.

      - Door panels shall have a minimum .125 inch (3.2 mm) structural wall thickness including adjoining horizontal members and perimeter frames where applicable.

        - Aluminum extrusions shall allow for factory installed, slide-in type weather-stripping.

      - Door Construction shall be by means of an integrated corner block with 1/2 inch all-thread through bolt from each stile.

      - Glass stops shall be .062 inch (15.8 mm) wall thickness and shall provide security function as a standard by means of a fixed non-removable exterior section with glazing to be performed from the interior only.

      - Vertical Stiles shall be [narrow stile 2-1/8 inch (54 mm).]  [medium stile 4 inch (102 mm).]  [wide stile 5 inch (127 mm).]

      - Bottom Rails shall be [4 inch (102 mm).]  [7 inch (178 mm).]  [10 inch (254 mm).]

      - [Intermediate Muntin shall be [1-3/4 inch (45 mm).]  [4 inch (102 mm).]

      - Weather-stripping:  Slide-in type, replaceable pile mohair seals retained by the aluminum extrusions.  Bottom rails shall be provided with an adjustable nylon sweep.

      - Glass:  Glazing shall comply with ANSI Z97.1, thickness as indicated.

- NOTE:  Select glazing types as required for the project.  Add “Locations” to each of the following if multiple types and/or thickness glazing is required.   Ex: Exterior vs Interior

        - Glazing Door Panels:  [1/4” (6 mm)] tempered glass, unless otherwise specified. [Optional glazing: 5/8” (16 mm) insulated glass, 1” (25 mm) insulated glass]

        - Glazing Transom Panel:  [1/4” (6 mm)] safety glass, unless otherwise specified.  [Optional glazing: 5/8” (16 mm) insulated safety glass, 1” (25 mm) insulated safety glass]

        - Glazing Installation:  See Division 8 Section “Glazing” for requirements.

          - [All Glazing furnished “by others”.]

    - Framing Members:  Provide automatic entrances as complete assemblies.  Manufacturer’s standard extruded aluminum framing reinforced as required to support loads.

      - Vertical Jambs shall be 1-3/4 inches (44.5 mm) by 4-1/2 inches (114.3 mm).

    - Header:  Manufacturer’s standard extruded aluminum header unit extending full width of entrance unit to conceal door operators.

      - Header Mounting:  Overhead concealed mounted header installed between jambs.

  - HARDWARE

    - Hardware:  Provide manufacturer’s standard hardware as required for operation indicated.

      - Bottom pivot assemblies and fingerguards shall be provided and comply with applicable codes.

- NOTE:  Consult SpecDesk for locking hardware options

      - Locking hardware shall be provided as indicated.

        - [Mortise type hookbolt latch. (Single swing door).]

          - Interior Side: [Thumbturn.]  [Keyed cylinder.]  Lock indicators shall be provided if required by code.

          - Exterior Side: [Keyed cylinder.]  [No cylinder.]

        - [Two point locking system with concealed vertical rod and mortise hookbolt. (Pair of swinging doors).]

          - Interior Side: [Thumbturn.]  [Keyed cylinder.]  Lock indicators shall be provided if required by code.

          - Exterior Side: [Keyed cylinder.]  [No cylinder.]

        - [Exit devices with concealed vertical rods.]

- NOTE:  Flush mounted exit devices require 4 inch horizontal muntin

          - Egress Side:  [Adams-Rite 8600 Series, concealed vertical rod exit device mounted to active doors.]  [Flush mounted Adams-Rite F86 Series, concealed vertical rod exit devices mounted to active doors.]

          - Entry Side:  [Entry trim with curved lever.]  [Thumbturn with keyed cylinder to retract vertical rod.]

      - Keyed cylinders shall be provided as indicated.

        - [Manufacturer’s standard keyed cylinder.]

        - [Keyed cylinder specified in Division 8 Section “Door Hardware”.]

        - [Keyed cylinder by others.]

    - [Threshold:  Manufacturer’s threshold as indicated.]

      - 1/2 inch (12.7 mm) high continuous aluminum threshold shall span the entire width of the opening and fit between the vertical framing members.  Threshold design shall allow for optional extruded ramps to securely interlock to flat section to meet ADA requirements.

        - [Surface mounted threshold with interlocking ADA accessible ramps.]  [Recessed mounted threshold.]

  - AUTOMATIC SWING DOOR OPERATOR

    - Model:  Besam ASSA ABLOY SW200i full energy automatic door operator (Basis of Design):]

- NOTE:  Select the following options as required for the project

      - Reference Standard:  ANSI/BHMA A156.10.

      - Configuration:  Operator to control single swinging doors and pairs of swinging doors as indicated on the drawings and specified below:

        - Pairs of Doors:  Simultaneous swing.

      - Automatic Door Operator:  Electro-mechanical, non-handed operator, powered by 24 volt, 1/4 hp motor.  Operator shall be adjustable to compensate for different manual push forces as required.

        - Automatic operator shall be capable of operating and controlling up to a 700 pound (317.5 kg) door, 48 inches (1219 mm) in width.

        - Overhead Concealed Mounted Operator:

          - Side Access Operator Housing: Operator is contained in a 6 inch (152.4 mm) x 6 inch (152.4 mm) high side access, extruded aluminum housing with a hinged cover for complete access to operator and internal electronic assemblies.

          - Overhead Concealed Mounted Housing:  Mounted between door jambs, continuous for full width of door.

          - Center Pivoted Door Connecting Hardware: Overhead concealed mounted operators to have a cast steel arm from the operator, concealed mounted to the top edge of the swing door.

- NOTE:  Select the following option if inswing center pivoted doors require breakaway for egress – verify compliance with the building code

            - [Emergency Breakaway:  Where inswing doors also serve as required exits, provide emergency breakaway feature to allow doors to swing in the direction of egress.  Forces to comply with ANSI/BHMA A156.10.  Discontinue power to automatic door operator when door is in emergency breakaway position, and to automatically reset when door is manually returned to the full closed position.]

        - Operator Temperature Range:  Capable of operating within temperature ranges of -31 F to 160 F (-35 C to 71 C).

        - Electrical Characteristics:  Maximum power consumption is 300 watts (2.5 amps at 120 VAC), 50/60hz, built-in thermal overload protection.

        - [Battery Convenience Mode:  Operator to maintain continuous operation by battery power during power failure. Battery is continuously monitored and provides a warning signal if the battery is not working properly.]

        - [Digital Cycle Counter:  Battery powered, 7 digit LCD cycle counter with a reset feature to track door usage cycles.]

      - Door Operation:

        - Opening Cycle The adjustable speed operator mechanically powers the drive shaft and the torque control maintains constant speed throughout the opening cycle regardless of stack pressures or wind speed.  Operator shall allow manual door operation with operational forces as indicated to fully open the door applied at 1” (25 mm) from the latch edge of the door.

          - Manual push force shall be adjustable from 5 lbf to 15 lbf maximum.

        - Hold Open:  The operator shall stop and hold the door open at the selected door opening angle for an adjustable period of time (1.5 seconds to 30 seconds).

        - Closing Cycle:  Spring close with speed controlled power assist.

          - Upon loss of power, dynamic braking will control the door insuring controlled closing.

          - Selectable Torque Control:  Automatically adjusts torque without changing the closing speed of the operator.

            - When the torque control is activated, the closing speed shall remain constant regardless of stack pressures or wind speed.

            - Torque Cancellation:  The torque control is deactivated whenever there is a signal received from door mounted sensors.

            - The torque control is disabled during manual use of the door.

        - Wind Force Dampening:  The operator electromechanically counteracts wind forces, slowing down the door movement to safely open or close the door.

        - Stack Pressure Compensation:  Operator shall counteract positive stack pressures, negative stack pressures, and sudden changes of stack pressures.  The operator never allows the door to open or close faster than the speed control settings, regardless of pressures.

        - Obstruction Control:  The operator will stop and reverse the door movement.

        - Electric Lock Management:

          - Internal module for electrified locking integration.

          - Electric Lock Output:  Selectable 12 VDC, maximum 1200 mA / 24 VDC, maximum 600 mA.

          - Lock monitoring prevents operator(s) from opening door(s) until release of electrified lock.

          - Operator pulls door closed before opening, automatically unjamming electric latch hardware.

          - Sequenced operation between operators for pairs of doors allowing lock release and astragal coordination.

        - Lock Retry Circuit:  If attempt to fully close the door is unsuccessful, the operator will automatically reverse open 10 degrees and reclose in an attempt to successfully close the door.

        - Selectable Alarm Reset:  The operator can be field set so that after receiving an alarm signal, the operator will not accept any activation impulses and will operate only as a manual door closer until manually reset.

        - Electronic Controls:  Solid state integrated circuit controls the operation and switching of the swing power operator.  The electronic control provides low voltage power supply for all means of actuation.  The controls include time delay (1 to 30 seconds) for normal cycle.

        - Control Switch: Automatic door operators shall be equipped with the following type of multi-position function switch:

          - [3 position toggle switch remotely mounted (On-Off-Hold).]

          - [4 position rotary switch remotely mounted (On-Off-Hold-Special Function).]

      - Operator Interface:

        - Safety Sensor Integration for overhead presence safety device and door mounted reactivation safety sensors.

  - ACTIVATION DEVICES

    - General:  Provide safety devices in accordance with ANSI/BHMA A156.10 standards, for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate safety devices with door operation and door operator mechanisms.

    - Automatic Activation Device:

      - Motion Sensors:  Self-contained, K-band-frequency, microwave-scanner unit; achieving both a narrow or wide sensing pattern, adjustable to provide detection field sizes and functions required by ANSI/BHMA A156.10.

        - Motion Sensors to offer three motion detection actions; bi-directional, uni-directional, and uni-MTF detection.

  - SAFETY DEVICES

    - General:  Provide safety devices in accordance with ANSI/BHMA A156.10 standards, for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate safety devices with door operation and door operator mechanisms.

- NOTE:  Select from one of the following the presence detection systems – Consult SpecDesk for safety device recommendations

- NOTE:  Presence detection is required by ANSI/BHMA A156.10 to provide safety at the doorway

    - Presence Detection Systems and Safety Devices:

- OPTION 1:  Select the following safety sensor system for maximum safety at the doorway, compliant with ANSI/BHMA A156.10 requirements

      - [ASSA ABLOY I-Adapt Premium Safety Sensor System A202 (Basis of Design), Door Mounted Presence Sensor Adaptable Field (DMPS-AF) as specified:]

        - Door Mounted Presence Sensor Adaptable Field (DMPS-AF): Door mounted combination activation motion sensor/safety presence sensor.  Sensor shall be mounted on both the swing (pull) side and the approach (push) side of the door (2 sensors per leaf).

- OPTION 1:  Select one of the following sensor technologies – “active infrared presence technology” is manufacturer’s default sensor;  “presence laser technology” is a secondary option.  Sensors for both selections are mounted on the upper hinged corner of the door and have a minimal footprint.

          - [Sensor shall utilize active infrared presence technology with auto adapting field to detect moving or stationary presence of people or objects in the swing path of the door.]   [Sensor shall utilize presence laser technology with auto adapting field to detect moving or stationary presence of people or objects in the swing path of the door.]

          - Presence detection shall always be active and remain active when the door is in motion.  The sensor provides a full detection pattern that covers the entire swing of the door and also provides detection in the full open and full close position.

          - The sensor has an auto adapting field which maximizes the sensor pattern tailored to the environment providing detection beyond the moving part of the door.  The sensor provides detection to the wall and or guide rails ensuring maximum safety resulting in the door stopping much sooner (further) from the person using the doorway.

          - Upon detection the sensor shall provide a signal to slow, stop, or reverse the door action depending on the situation.

          - The sensor provides secondary activation as required for “knowing act” doorways.

          - Since the infrared presence detection is always active, no overhead safety sensor is required.

          - Motion/presence detecting sensors to be field installed and adjusted.

- OPTION 2:  Select the following safety sensor system for safety at the doorway, compliant with ANSI/BHMA A156.10 requirements

      - [ASSA ABLOY I-Adapt Flex Safety Sensor System A102 (Basis of Design), Combination of an Overhead Presence Sensor (OPS) and Door Mounted Presence Sensors (DMPS) as specified:]

        - Overhead Presence Sensor (OPS):  Header mounted, overhead presence sensor utilizing infrared technology for detection; adjustable to provide detection field sizes and functions required by ANSI/BHMA A156.10.  Unit to provide the following two independently adjustable patterns of detection:

          - The door closed position covering the area on the swing side of the door.

          - The door open position including an area of detection that reaches through the threshold toward the non-swing side of the door.

          - The unit is not active during the door closing cycle.

        - Door Mounted Presence Sensor (DMPS):  Door mounted infrared presence safety device (mounted at top of each door); adjustable to provide detection field sizes and functions required by ANSI/BHMA A156.10.

          - The door mounted presence detector shall be mounted on both the swing (pull) side and the approach (push) side of the door (2 sensors per leaf), providing detection on both sides of the door.

          - Unit to provide detection during the travel of the door.

          - Upon detection the sensor shall provide a signal to stop or reverse the door action.

          - [Door mounted presence sensor shall be monitored, providing a supervisory circuit to the operator.]

- OPTION 3:  Select the following safety sensor system for safety at the doorway, compliant with ANSI/BHMA A156.10 requirements

      - [ASSA ABLOY I-Adapt Flex Safety Sensor System A101 (Basis of Design), Combination of an Overhead Presence Sensor (OPS) and a Door Mounted Presence Sensor (DMPS) as specified:]

        - Overhead Presence Sensor (OPS):  Header mounted, overhead presence sensor utilizing infrared technology for detection; adjustable to provide detection field sizes and functions required by ANSI/BHMA A156.10.  Unit to provide the following two independently adjustable patterns of detection:

          - The door closed position covering the area on the swing side of the door.

          - The door open position including an area of detection that reaches through the threshold toward the non-swing side of the door.

          - The unit is not active during the door closing cycle.

        - Door Mounted Presence Sensor (DMPS):  Door mounted infrared presence safety device (mounted at top of each door); adjustable to provide detection field sizes and functions required by ANSI/BHMA A156.10.

          - The door mounted presence detector shall be mounted on the swing (pull) side of the door (1 sensor per leaf), providing detection on one side of the door only.

            - On “knowing act” double egress doorways, the door mounted presence detector shall be mounted on the approach (push) side of the door (1 sensor per leaf).

          - Unit to provide detection during the travel of the door.

          - Upon detection the sensor shall provide a signal to stop or reverse the door action.

          - [Door mounted presence sensor shall be monitored, providing a supervisory circuit to the operator.]

  - [ACCESSORIES]

- NOTE:  ANSI/BHMA A156.10 requires guide rails for power operated swing doors unless the door is located adjacent to a wall – Consult SpecDesk for guide rail requirements - delete this section if not required

    - [Guide Rails:  [Anodized aluminum]  [Painted aluminum]  [Stainless steel], fabricated from  [bars]  [tubing], minimum 30 inches (762 mm) high, and finished to match doors unless otherwise indicated; positioned and projecting from face of door jamb for distance as indicated, but not less than that required by ANSI/BHMA A156.10 for type of door and direction of travel; with filler panel.]

      - Filler Panel:  [Expanded aluminum mesh.]  [Polycarbonate plastic.]

        - Orient expanded aluminum mesh with long dimension of diamonds [parallel to top rail.]  [perpendicular to top rail.]  [horizontal.]  [vertical.]

        - Color: [To match guide rails.]  [Clear.]  [As indicated by manufacturer's designations.]  [Match Architect's sample.]

      - Mounting:  [Jamb and floor.]  [Floor, freestanding.]

- NOTE:  If the following is retained, provide details

    - [Guide Rails:  To be as detailed (see architectural drawings).]

    - Guide Rail Finishes:

      - [Anodized Finish:]

        - [AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

        - [AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

        - [AAMA 611, Custom anodized to match architect’s sample.]

      - [Painted Finish:]

        - [Powder coat painted to match architect’s sample.]

        - [Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

      - [Stainless Steel Finish:]

        - Stainless steel with a satin finish.

      - [To match architects sample.]

  - ALUMINUM FINISHES

- NOTE:  Consult SpecDesk for custom finish options

    - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

    - [Anodized Finish:]

      - [AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

      - [AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

      - [AAMA 611, Custom anodized to match architect’s sample.]

    - [Painted Finish:]

      - [Powder coat painted to match architect’s sample.]

      - [Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

    - [Clad Finish (protective coatings by others):]

      - [Stainless steel with #4 satin finish.]

      - [Stainless steel with #8 mirrorlike, reflective, non-directional finish.]

      - [Bronze with a satin finish.]

      - [Bronze with a polished, non-directional finish.]

      - [Brass with a satin finish.]

      - [Brass with a polished, non-directional finish.]

    - [To match architects sample.]

- EXECUTION

  - EXAMINATION

    - Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance.

    - Examine roughing-in for electrical source power to verify actual locations of wiring connections.

    - Proceed only after such discrepancies or conflicts have been resolved.

  - INSTALLATION

    - Do not install damaged components.  Fit frame joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Entrances:  Install automatic entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

      - Install surface mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, operators, operating brackets and guides level and true to location with anchorage for permanent support.

    - Door Operators:  Connect door operators to electrical power distribution system as specified in Division 26 Sections.

    - Glazing:  Glaze swinging automatic entrance door panels in accordance with the Glass Association of North America (GANA) Glazing Manual, published recommendations of glass product manufacturer, and published instructions of automatic entrance system manufacturer.

    - Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to provide a weather tight installation.

      - Set thresholds, bottom guide and track systems and framing members in full bed of sealant.

      - Seal perimeter of framing members with sealant.

    - Signage:  Apply signage on both sides of each door and sidelite as required by ANSI/BHMA A156.10 and manufacturers installation instructions.

  - ADJUSTING

    - Adjust door operators, controls and hardware for smooth and safe operation and for weather tight closure. Adjust doors in compliance with ANSI/BHMA A156.10.

    - Verify installation and alignment of all entrance weather-stripping as required for compliance with specified air infiltration requirements.

  - FIELD QUALITY CONTROL

    - Before placing doors into operation, AAADM certified technician shall inspect and approve doors for compliance with ANSI/BHMA A156.10. Certified technician shall be approved by the manufacturer.

  - CLEANING AND PROTECTION

    - Clean adjacent surfaces soiled by door installation.

    - Clean glass and metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages to match original finish.

  - DEMONSTRATION

    - Engage a factory-authorized representative to train Owner's maintenance personnel to adjust, operate, and maintain safe operation of the door.

END OF SECTION