SECTION 08 42 43 – INTENSIVE CARE UNIT/CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

- GENERAL

  - SUMMARY

- NOTE:  Edit this specification as required for the project

    - This section includes the following types of intensive care unit/critical care unit (ICU/CCU) entrance doors:

      - [Swing / bi-fold combination ICU/CCU entrance.]

      - [Bi-fold ICU/CCU entrance.]

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - Division 8 Section “Glazing” for materials and installation requirements of glazing for ICU/CCU entrance doors.

  - REFERENCES

    - References:  Refer to the version year adopted by the Authority Having Jurisdiction.

      - ANSI A117.1 - Accessible and Usable Buildings and Facilities.

      - ICC/IBC - International Building Code.

      - NFPA 70 - National Electrical Code.

      - NFPA 101 - Life Safety Code.

- NOTE:  Delete the following if smoke control entrances are not required

      - [NFPA 105 - Installation of Smoke Door Assemblies.]

    - American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA).

      - ANSI Z97.1 Standards for Safety Glazing Material Used in Buildings.

    - [Underwriters Laboratories (UL).]

- NOTE:  Delete the following if smoke control entrances are not required

      - [UL 1784 – Air Leakage Tests of Door Assemblies.]

    - American Society for Testing and Materials (ASTM).

      - ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.

      - ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.

    - American Architectural Manufacturers Association (AAMA).

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

    - National Association of Architectural Metal Manufacturers (NAAMM).

      - Metal Finishes Manual for Architectural Metal Products.

    - International Code Council (ICC).

      - [IBC:  International Building Code.]

      - [CBC: California Building Code.]

  - PERFORMANCE REQUIREMENTS

    - Compliance with the following:

- NOTE:  Delete the following if MicroShield is not required

    - [MicroShieldTM antimicrobial silver-based ion finish on all exposed surfaces including door pulls, door extrusions, rails and header to comply with the manufacturer’s specified requirements.]

      - Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew.

  - SUBMITTALS

    - Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.

    - Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, and fabrication of doors, frames, sidelites, hardware, finish, options and accessories.

    - Samples: Submit manufacturer’s samples of aluminum finish.

    - Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification.

      - Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

    - Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the complete door opening installation in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the entrance and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.

    - Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.

  - QUALITY ASSURANCE

    - Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.  Manufacturer to have a company certificate issued by AAADM.

    - Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum 5 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

    - Source Limitations for ICU/CCU Entrances:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.

  - PROJECT CONDITIONS

    - Field Measurements:  Verify actual dimensions of openings to receive ICU/CCU entrances by field measurements before fabrication and indicate on shop drawings.

  - COORDINATION

    - Coordinate sizes and locations of recesses in concrete floors for recessed tracks and thresholds if applicable. Concrete work is specified in Division 03.

  - WARRANTY

    - General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

    - ICU/CCU entrances shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

- PRODUCTS

  - MANUFACTURER

    - Manufacturer:  ASSA ABLOY Entrance Systems, 1900 Airport Road, Monroe, NC 28110. Toll Free (877) SPEC-123.  Fax (704 ) 290- 5555 Website www.assaabloyentrance.us contact: specdesk.na.entrance@assaabloy.com

- NOTE:  Revise the following substitution clause as required by project requirements.  Select either Item “B” or “C”

    - [Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

    - [Substitutions:  Not Permitted.]

  - INTENSIVE CARE UNIT/CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

    - ICU/CCU entrances including the following:

      - Swinging panels, bi-fold panels, and aluminum frame.

      - Entrance header, guide system and carrier assemblies.

- NOTE:  Select entrance configuration(s) as required for the project

    - Besam ASSA ABLOY VersaMax® 2.0 ICU/CCU Fold Door Package (Basis of Design):

      - [ICU/CCU 3 panel, non-latching folding/swing door system.]

        - Operation:  Manually operated, non-latching.

        - Door Configuration:  Double-acting swing door and a 2 panel bi-fold door combination.

          - Swing Door:  Non-latching, double-acting door with door closer.

          - Bi-Fold Door:  Non-latching, 2 panel, bi-fold door.

        - Breakaway Capability:  Bi-fold door to have break-out from any position.

        - Mounting:  Overhead header installed between jambs.

        - Trackless Design:  Floor mounted guide track not allowed.

      - [ICU/CCU 3 panel, latching folding/swing door system.]

        - Operation:  Manually operated, latching.

        - [Smoke Seals:  Smoke gasketing that meets the infiltration requirements of UL1784.]

        - Door Configuration:  Directional swing door and a 2 panel bi-fold door combination.

          - Swing Door:  Latching, directional swing door with door closer.

          - Bi-Fold Door:  Latching 2 panel, bi-fold door.

        - Breakaway Capability:  Bi-fold door to have break-out from any position.

        - Mounting:  Overhead header installed between jambs.

        - Trackless Design:  Floor mounted guide track not allowed.

      - [ICU/CCU 2 panel, folding door system.]

        - Operation:  Manually operated.

        - Door Configuration:  2 panel bi-fold door.

        - Breakaway Capability:  Bi-fold door to have break-out from any position.

        - Mounting:  Overhead header installed between jambs.

        - Trackless Design:  Floor mounted guide track not allowed.

      - [ICU/CCU 4 panel, folding door system.]

        - Operation:  Manually operated.

        - Door Configuration:  Two 2 panel bi-fold doors.

        - Breakaway Capability:  Bi-fold door to have break-out from any position.

        - Mounting:  Overhead header installed between jambs.

        - Trackless Design:  Floor mounted guide track not allowed.

  - ENTRANCE COMPONENTS

    - Stile and Rail Sliding/Swing/Folding Panels and Sidelites:

      - Material:  Extruded Aluminum, Alloy 6063-T5 or 6063-T6.

      - Door panels shall have a minimum .125 inch (3.2 mm) structural wall thickness including adjoining perimeter frames where applicable.

        - Aluminum extrusions shall allow for a factory installed, slide-in type gasket.

      - Door Construction shall be by means of an integrated corner clip with 3/8 inch diameter all-thread through bolt from each stile.

        - Face of door stiles shall be flush with adjacent rails and muntin.

      - Glass stops shall be .062 inch (15.8 mm) wall thickness and shall provide security function as a standard by means of a fixed non-removable exterior section with glazing to be performed from the interior only.

- NOTE:  Beveled glass stops available only with 1/4" glazing

        - [Beveled glass stops.]

      - Vertical Stiles shall be narrow stile 2-1/8 inch (54 mm).

      - Top Rail shall be 4 inch (102 mm).

      - Bottom Rails shall be [4 inch (102 mm).]  [7 inch (178 mm).]  [10 inch (254 mm).]

- NOTE:  Intermediate muntin option required with integral blinds

      - [Intermediate Muntin shall be [1-3/4 inch (45 mm).]  [4 inch (102 mm).]

      - [Gasketing:  Slide-in type, replaceable pile mohair seals.]

        - Bottom rails shall be provided with a concealed adjustable sweep gasket.

- NOTE:  Retain above “Gasketing” if the ICU/CCU entrances do not need to restrict smoke infiltration

- NOTE:  Retain “Smoke Gasketing” below if the ICU/CCU entrances need to restrict smoke infiltration

- NOTE:  The VersaMax Fold entrance is not certified to UL 1784 – the smoke gasketing meets the infiltration requirements of UL 1784

      - [Smoke Gasketing:  Slide-in type, replaceable, smoke type gasket that is capable of withstanding 400o F for a minimum of 30 minutes.]

        - Bottom rails shall be provided with a concealed adjustable sweep gasket that is capable of withstanding exposure to 400o F for a minimum of 30 minutes.

      - Glass:  Glazing for Sliding/Swing/Fold Panels and Sidelite Panels shall comply with ANSI Z97.1, thickness as indicated.

- NOTE:  Select glazing types as required for the project.  Add “Locations” to each of the following if multiple types and/or thickness glazing is required.

        - Glazing:  [1/4” (6 mm)] tempered glass, unless otherwise specified.  [Optional glazing: 5/8” (16 mm) insulated glass, 1” (25 mm) insulated glass, 1-1/4” (31 mm) insulated glass]

          - Glazing Installation:  Dry glazing; wet glazing not allowed.

            - See manufacturer’s instructions and Division 8 Section “Glazing” for requirements.

            - [All Glazing furnished “by others”.]

- NOTE:  Consult SpecDesk for integral blind information – glazing by ASSA ABLOY

- NOTE:  Consider a lower panel with opaque glazing when specifying integral blinds – delete if not required

        - [Lower Lite Glazing Panels:  1” (25 mm) overall thickness frosted insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.]

          - Frosted Glazing:  Opaque, acid etched on #2 or #3 surface.

        - [Upper Lite]  Glazing with Integral Blinds:  1-1/4” (31 mm) overall thickness insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.]

          - Integral Blinds:  Glass to have blinds installed between glass lites.

            - Blinds to be mechanically gear-driven tilt micro-blind installed in the sealed insulating glass unit.  Internally mounted control assembly that is coupled to the external operator controls the tilting of blind slats.

            - Tilt Operator:  Thumb wheel, dual control.

          - Glazing Installation:  Dry glazing; wet glazing not allowed.

            - See manufacturer’s instructions and Division 8 Section “Glazing” for requirements.

    - Framing Members:  Provide ICU/CCU entrances as complete assemblies.  Manufacturer’s standard extruded aluminum framing reinforced as required to support loads.

      - Vertical Jambs:  [1-3/4 inches (44.5 mm)]  [1 inch (25.4 mm)] by 4-1/2 inches (114.3 mm).]

    - Header:  Extruded aluminum header with track surface mounted under header, extending full width of entrance unit.

      - Header Capacity:  Capable of supporting up to 115 pounds (52.2 kg) weight of swing door and up to 170 pounds (77.1 kg) weight of folding door(s).

        - Size:  4-1/2 inches (114.3 mm) wide by 1-3/4 inches (44.5 mm) high.

  - HARDWARE

    - Hardware:  Provide manufacturer’s standard hardware as required for operation indicated.

- NOTE:  Non-latching, double acting swing door is standard – requires non-latching bi-fold door  – not available with smoke seal package

      - [Double-Acting Swing Door, Non-Latching:]

        - Top and bottom pivots.

        - Double acting door closer.

- NOTE:  Select the following if hold open feature is required

          - [Door closer shall have a 90 degree hold open feature (hold open in both directions).]

        - Manufacturer’s surface-mounted, vertical C-shaped pull handles on both sides of door.

- NOTE:  Optional positive latching for swing door  – requires latching bi-fold door

- NOTE:  This option is required if the entrance needs to restrict smoke infiltration – available only on the folding/swing door entrance

      - [Directional Swing Door, Latching:]

        - Top and bottom pivots.

        - Door closer.

- NOTE:  Select the following if hold open feature is required

          - [Door closer shall have a 90 degree hold open feature.]

        - Latching Hardware:  Concealed top and bottom vertical rods.  Bottom rod to serve as a counter balance mechanism, factory adjusted so that it does not extend below the bottom of the rail.

          - Push Side:  Push paddle.

          - Pull Side:  Curved lever handle.

- NOTE:  Non-latching, bi-fold door is standard  – requires non-latching swing door when folding/swing entrance

- NOTE:  Specify this option with the two panel / four panel bi-fold door entrances

      - [Two Panel / Four Panel Bi-Fold Door(s), Non-Latching:]

        - Top and bottom pivot(s).

        - One (1) rubber (Hytrel) roller wheel on the slave leaf(s).

        - Manufacturer’s surface-mounted, vertical C-shaped pull handle(s) on pull side of door(s).

        - Manufacturer’s surface-mounted, horizontal push bar(s) on push side of door(s).

        - Full height finger guard between folding door panels.

- NOTE:  Latching bi-fold door is required on the folding/swing door entrance when the latching swing door is specified

- NOTE:  This option is not available on the two panel / four panel bi-fold door entrances which do not have a swing door

      - [Two Panel Bi-Fold Door(s), Latching:]

        - Top and bottom pivot(s).

        - One (1) rubber (Hytrel) roller wheel on the slave leaf(s).

        - Manufacturer’s surface-mounted, vertical C-shaped pull handle(s) on pull side of door(s).

        - Manufacturer’s surface-mounted, horizontal push bar(s) on push side of door(s).

        - Full height finger guard between folding door panels.

      - Floor Mounted Guide Track/Threshold:

        - Trackless Design:  Floor mounted guide track and threshold not allowed.

  - ALUMINUM FINISHES

- NOTE:  Consult SpecDesk for custom finish options

    - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

    - [Anodized Finish:]

      - [AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

      - [AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

      - [AAMA 611, Custom anodized to match architect’s sample.]

    - [Painted Finish:]

      - [Powder coat painted to match architect’s sample.]

      - [Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

    - [To match architects sample.]

- NOTE:  Delete following if MicroShield is not required.  Consult SpecDesk for availability of MicroShield with anodized and painted aluminum finishes

    - [MicroShieldTM antimicrobial silver-based ion, baked-on enamel finish on all exposed surfaces including door pulls, door extrusions, rails and header.]

      - Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew by the controlled release of silver ions that attack microbes and inhibit the growth on the treated surfaces.

      - Coating to be EPA registered resulting in a safe and non-toxic finish; chlorinated or synthetic chemical finishes will not be accepted.

- EXECUTION

  - EXAMINATION

    - Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance.

    - Proceed only after such discrepancies or conflicts have been resolved.

  - INSTALLATION

    - Do not install damaged components.  Fit frame joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Install intensive care unit/critical care unit (ICU/CCU) entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

      - Install surface mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, carrier assemblies, tracks, operating brackets and guides level and true to location with anchorage for permanent support.

      - Where aluminum will contact dissimilar metals, concrete, or masonry, protect against galvanic action and corrosion.

- NOTE:  Delete the following if smoke control openings are not required

      - [Where smoke control intensive care unit/critical care unit (ICU/CCU) entrances are installed in smoke barriers or partitions, set framing members and header in a bed of sealant to comply with NFPA 105.]

    - Glazing:  Glaze intensive care unit/critical care unit (ICU/CCU) entrance door panels in accordance with the Glass Association of North America (GANA) Glazing Manual, published recommendations of glass product manufacturer, and published instructions of ICU/CCU entrance manufacturer.

    - Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to provide a weather tight installation.

      - Set thresholds and framing members in full bed of sealant.

      - Seal perimeter of framing members with sealant.

  - ADJUSTING

    - Adjust alignment of entrances and hardware for smooth, safe operation with minimum air infiltration.

    - Verify installation and alignment of all entrance gasketing as required for minimum air infiltration and compliance with specified standards.

  - CLEANING AND PROTECTION

    - Clean adjacent surfaces soiled by door installation.

    - Clean glass and metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages to match original finish.

  - DEMONSTRATION

    - Engage a factory-authorized representative to train Owner's maintenance personnel to adjust, operate, and maintain safe operation of the door.

END OF SECTION