SECTION 08 42 43 – INTENSIVE CARE UNIT/CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

- GENERAL

  - SUMMARY

- NOTE:  Edit this specification as required for the project

    - This section includes the following types of intensive care unit/critical care unit (ICU/CCU) entrance doors:

      - Power operated swing ICU/CCU entrances.

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - Division 8 Section “Glazing” for materials and installation requirements of glazing for ICU/CCU entrance doors.

      - Division 26 and 28 Sections for electrical connections including conduit and wiring for sliding door operators.

  - REFERENCES

    - References:  Refer to the version year adopted by the Authority Having Jurisdiction.

      - ANSI A117.1 - Accessible and Usable Buildings and Facilities.

      - ICC/IBC - International Building Code.

      - NFPA 70 - National Electrical Code.

      - NFPA 101 - Life Safety Code.

    - American National Standards Institute (ANSI) / Builders Hardware Manufacturers Association (BHMA).

      - ANSI/BHMA A156.19 Standards for Power Assist and Low Energy Power Operated Doors.

      - ANSI/BHMA A156.10 American National Standard for Power Operated Pedestrian Doors.

      - ANSI Z97.1 Standards for Safety Glazing Material Used in Buildings.

    - Underwriters Laboratories (UL).

      - UL Listed R-9469 Fire Door Operator with Automatic Closer.

      - UL 325 Standard for Safety for Door, Drapery, Gate, Louver and Window Operators and Systems.

      - UL 991 Listed - Tests for Safety-Related Controls Employing Solid-State Devices.

    - American Society for Testing and Materials (ASTM).

      - ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.

      - ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.

    - American Architectural Manufacturers Association (AAMA).

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

    - National Association of Architectural Metal Manufacturers (NAAMM).

      - Metal Finishes Manual for Architectural Metal Products.

    - International Code Council (ICC).

      - [IBC:  International Building Code.]

      - [CBC: California Building Code.]

  - DEFINITIONS

    - Activation Device: Device that, when actuated, sends an electrical signal to the door operator to activate the operation of the door.

      - Knowing act:	Consciously initiating the opening of a power operated door using acceptable methods including wall mounted switches such as push plates and controlled access devices such as keypads, card readers and key switches.

    - Safety Device: A device that detects the presence of an object or person within a zone where contact could occur and provides a signal to stop the movement of the door.

  - PERFORMANCE REQUIREMENTS

    - Compliance with the following:

      - ANSI/BHMA A156.19 Standards for Power Assist and Low Energy Power Operated Doors.

    - Opening Force Requirements:  Doors shall open with a manual force, not to exceed 30lbf (133N) to set the door in motion and 15 lbf to fully open the door applied at 1” (25 mm) from the latch edge of the door.  The force required to prevent a stopped door from opening or closing shall not exceed 15 lbf (67 N) measured 1” (25 mm) from the latch edge of the door at any point during opening or closing.

    - Closing Time:

      - Doors shall be field adjustable to close from 90 degrees to 10 degrees in 3 seconds or longer as applicable per ANSI/BHMA A156.19 standards.

      - Doors shall be field adjusted to close from 10 degrees to fully closed in not less than 1.5 seconds.

- NOTE:  Delete the following if MicroShield is not required

    - [MicroShieldTM antimicrobial silver-based ion finish on all exposed surfaces including door pulls, door extrusions, rails and header to comply with the manufacturer’s specified requirements.]

      - Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew.

  - SUBMITTALS

    - Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.

    - Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, and fabrication of doors, frames, operator, presence sensor, activation device, anchors, hardware, finish, options and accessories.

    - Samples: Submit manufacturer’s samples of aluminum finish.

    - Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification.

      - Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

    - Manufacturers Field Reports:  Submit manufacturer’s field reports from AAADM certified technician of inspection and approval of doors for compliance with ANSI/BHMA A156.19 after completion of installation.

    - Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the complete door opening installation in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the entrance and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.

    - Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.

  - QUALITY ASSURANCE

    - Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.  Manufacturer to have a company certificate issued by AAADM.

    - Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum 5 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

    - Certified Inspector Qualifications: Certified by AAADM.

    - Source Limitations for ICU/CCU Entrances:  Obtain each type of door, frame, operator and sensor components specified in this Section from a single source, same manufacturer unless otherwise indicated.

    - Certifications: Operators shall be certified by the manufacturer to meet performance design criteria in accordance with the following standards.

      - ANSI/BHMA A156.19 American National Standard for Power Assist and Low Energy Operated Doors.

      - NFPA 101 - Life Safety Code.

      - UL 325 - Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

    - Emergency Exit door requirements: Comply with requirements of authorities having jurisdiction for ICU/CCU entrances serving as a required means of egress.

  - PROJECT CONDITIONS

    - Field Measurements:  Verify actual dimensions of openings to receive ICU/CCU entrances by field measurements before fabrication and indicate on shop drawings.

  - COORDINATION

    - Coordinate sizes and locations of recesses in concrete floors for recessed tracks and thresholds if applicable. Concrete work is specified in Division 03.

    - Electrical System Roughing-in: Coordinate layout and installation of power operated ICU/CCU entrances with connections to power supplies and access control system as applicable.

  - WARRANTY

    - General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

    - ICU/CCU entrances shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

    - During the warranty period a factory-trained technician shall perform service and affect repairs. An inspection shall be performed after each adjustment or repair.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.

    - Manufacturer shall have in place a dispatch procedure that shall be available 24 hours a Day, 7 Days a week for emergency call back service.

- PRODUCTS

  - MANUFACTURER

    - Manufacturer:  ASSA ABLOY Entrance Systems, 1900 Airport Road, Monroe, NC 28110. Toll Free (877) SPEC-123.  Fax (704 ) 290- 5555 Website www.assaabloyentrance.us contact: specdesk.na.entrance@assaabloy.com

- NOTE:  Revise the following substitution clause as required by project requirements.  Select either Item “B” or “C”

    - [Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

    - [Substitutions:  Not Permitted.]

  - INTENSIVE CARE UNIT/CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

    - ICU/CCU entrances including the following:

      - Swinging panels and aluminum frame.

      - Entrance header.

      - Overhead electro-mechanical operator.

      - Controls, door hardware and accessories as required for a complete installation.

- NOTE:  Select entrance configuration(s) as required for the project

    - Besam ASSA ABLOY VersaMax® 2.0 ICU/CCU Swing Door Package (Basis of Design):

      - Swing ICU/CCU door system.

        - Operation:  Manually operated, self-latching with power operator.

        - Configuration:  Configuration(s) as indicated on the drawings and below.

          - [Unequal Pair of Swing Doors:  One active leaf (primary panel) and one inactive leaf (secondary panel).]

          - [Pair of Swing Doors:  Two active leaves (both primary panels).]

          - [Single Swing Door:  One active leaf (primary panel).]

        - Mounting:  Overhead header installed between jambs.

  - ENTRANCE COMPONENTS

    - Stile and Rail Sliding/Swing/Folding Panels and Sidelites:

      - Material:  Extruded Aluminum, Alloy 6063-T5 or 6063-T6.

      - Door panels shall have a minimum .125 inch (3.2 mm) structural wall thickness including adjoining perimeter frames where applicable.

        - Aluminum extrusions shall allow for a factory installed, slide-in type gasket.

      - Door Construction shall be by means of an integrated corner clip with 3/8 inch diameter all-thread through bolt from each stile.

        - Face of door stiles shall be flush with adjacent rails and muntin.

      - Glass stops shall be .062 inch (15.8 mm) wall thickness and shall provide security function as a standard by means of a fixed non-removable exterior section with glazing to be performed from the interior only.

- NOTE:  Beveled glass stops available only with 1/4" glazing

        - [Beveled glass stops.]

      - Vertical Stiles shall be [narrow stile 2-1/8 inch (54 mm).]  [medium stile 4 inch (102 mm).]

      - Bottom Rails shall be [4 inch (102 mm).]  [7 inch (178 mm).]  [10 inch (254 mm).]

      - [Intermediate Muntin shall be [1-3/4 inch (45 mm).]  [4 inch (102 mm).]

      - Gasketing:  Slide-in type, replaceable pile mohair seals.

        - Bottom rails shall be provided with a concealed adjustable sweep gasket.

      - Glass:  Glazing for Sliding/Swing/Fold Panels and Sidelite Panels shall comply with ANSI Z97.1, thickness as indicated.

- NOTE:  Select glazing types as required for the project.  Add “Locations” to each of the following if multiple types and/or thickness glazing is required.

        - Glazing:  [1/4” (6 mm)] tempered glass, unless otherwise specified.  [Optional glazing: 5/8” (16 mm) insulated glass, 1” (25 mm) insulated glass, 1-1/4” (31 mm) insulated glass]

          - Glazing Installation:  Dry glazing; wet glazing not allowed.

            - See manufacturer’s instructions and Division 8 Section “Glazing” for requirements.

            - [All Glazing furnished “by others”.]

- NOTE:  Consult SpecDesk for integral blind information – glazing by ASSA ABLOY

- NOTE:  Consider a lower panel with opaque glazing when specifying integral blinds – delete if not required

        - [Lower Lite Glazing Panels:  1” (25 mm) overall thickness frosted insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.]

          - Frosted Glazing:  Opaque, acid etched on #2 or #3 surface.

        - [Upper Lite]  Glazing with Integral Blinds:  1-1/4” (31 mm) overall thickness insulating glass unit consisting of an interior and exterior glass lite; both lites to be 1/4 inch (6 mm) tempered glass.]

          - Integral Blinds:  Glass to have blinds installed between glass lites.

            - Blinds to be mechanically gear-driven tilt micro-blind installed in the sealed insulating glass unit.  Internally mounted control assembly that is coupled to the external operator controls the tilting of blind slats.

            - Tilt Operator:  Thumb wheel, dual control.

          - Glazing Installation:  Dry glazing; wet glazing not allowed.

            - See manufacturer’s instructions and Division 8 Section “Glazing” for requirements.

    - Framing Members:  Provide ICU/CCU entrances as complete assemblies.  Manufacturer’s standard extruded aluminum framing reinforced as required to support loads.

      - Vertical Jambs:  [1-3/4 inches (44.5 mm)]  [1 inch (25.4 mm)]  by 4-1/2 inches (114.3 mm).

    - Header:  Extruded aluminum header shall have a minimum .109 inch (2.8 mm) structural wall thickness and shall extend the full width of entrance.

      - Size:  [Standard ICU header - 4-1/2 inches (114.3 mm) wide by 4-1/2 inches (114.3 mm) high.]  [Low profile header - 4-1/2 inches (114.3 mm) wide by 1-3/4 inches (44.5 mm) high.]

  - HARDWARE

    - Hardware for Swinging Entrances:  Provide manufacturer’s standard hardware as required for operation indicated.

      - Hinges:  Half mortise, gear type, continuous hinge; allows 180o swing.

      - Door Pulls:  Manufacturer’s surface-mounted, 10” C-shaped, door pull installed on both sides of active door leave(s).

      - Latching hardware shall be provided as indicated.

        - Active Door Leaves:  Roller latch mounted in the top door rail.

        - Inactive Leaf:  Manual operated flush bolt.

  - SWING DOOR LOW ENERGY DOOR OPERATOR

    - Model:  ASSA ABLOY SW100 low energy automatic door operator (Basis of Design):

      - Reference Standard:  ANSI/BHMA A156.19.

      - Configuration:  Operator to control single swinging doors and pairs of swinging doors as indicated on the drawings and specified below:

        - Pairs of Doors:  Simultaneous swing (both leaves active).

      - Automatic Door Operator:  Electro-mechanical, non-handed operator, powered by 24 volt, 1/8 hp motor.  Spring shall be adjustable to compensate for different manual push forces required on varying door widths.

        - Automatic operator shall be capable of operating and controlling up to a 200 pound (91 kg) door, 48 inches (1219 mm) in width.

        - Surface Mounted Operator:

          - Side Access Operator Housing:  Operator is contained in 5-1/8” (130.2 mm) deep x 4 5/16” (110 mm) high extruded aluminum housing with a removable cover.

          - Surface Mounted Housing:  Continuous for full width of door.

          - Connecting Hardware: Surface mounted operators to have a steel arm from the operator, mounted to the top face of the swing door.

          - UL Listed R-9469 Fire Door Operator with Automatic Closer (surface mounted operator).

        - Operator Temperature Range:  Capable of operating within temperature ranges of -20F (-29C) and 160F (71C).

        - Electrical Characteristics:  Nominal current draw 75 watts (.625 amps at 120 VAC), built-in thermal overload protection.

        - [Battery Convenience Mode:  Operator to maintain continuous operation by battery power during power failure. Battery is continuously monitored and provides a warning signal if the battery is not working properly.]

      - Door Operation:

        - Opening Cycle:  The adjustable speed operator shall control the door opening to the back check position, where the opening speed is reduced.

          - Manual door operation with operational forces of 15 lbf maximum to fully open the door applied at 1” (25 mm) from the latch edge of the door.

        - Hold Open:  The operator shall stop and hold the door open at the selected door opening angle for an adjustable period of time (1.5 seconds to 30 seconds).

        - Closing Cycle:  Power closing shall be provided by means of clock spring and motor.  The door will slow to low speed at latch check before it reaches the fully closed position.

        - Electronic Dampening:  Operator to include standard electric dampening system which automatically counteracts additional forces applied to the door during the opening or closing cycle by reducing door speed.

        - Stack Pressure Compensation:  Electronic control allows for increases of forces to overcome minor stack pressures while compensating to lower manual push forces when the door is used in manual mode in order to comply with ANSI/BHMA A156.19.

        - Obstruction Control:  The operator will stop and reverse the door movement.

        - Astragal Coordinator:  Sequenced electronic operation between operators for pairs of doors allowing astragal coordination.

        - Lock Retry Circuit:  If attempt to fully close the door is unsuccessful, the operator will automatically reverse open 10 degrees and reclose in an attempt to successfully close the door.

        - Electronic Controls:  Microprocessor controlled unit shall control the operation and switching of the swing power operator.  The microprocessor unit provides low voltage power supply for all means of actuation.  The controls include time delay (1.5 to 30 seconds) for normal cycle.

        - Control Switch: Automatic door operators shall be equipped with the following type of multi-position function switch:

- NOTE:  Select one of the following control switch options

          - [3 position rocker switch mounted on end cap (On-Off-Hold).]

          - [2 position rocker switch mounted on end cap (On-Off).]

      - [Operator Interface:]

        - Safety Sensor Integration for overhead presence safety device and door mounted reactivation safety sensors.

- NOTE:  Select the type of activation devices and safety devices required for the project

  - SWING DOOR ACTIVATION AND SAFETY CONTROL DEVICES

    - Activation Devices:  Provide activation and safety devices in accordance with ANSI/BHMA standards, for condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate activation and safety devices with door operation and door operator mechanisms.

      - [Knowing Act Activation Device:]

        - [Push Plate:  Hard wired, [4-1/2 inch square]  [6 inch round] stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

        - [Push Plate:  Jamb mounted, hard wired, 1-1/2 inch x 4-3/4 inch, stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

        - [Push Plate:  Radio controlled, wireless, [4-1/2 inch square]  [6 inch round]   stainless steel push plate switches engraved with "Push to Open" with a blue handicap logo.]

        - [Sensor Plate:  Touchless, [2-3/4 inch x 4-1/2 inch]  [4-1/2 inch square] activation senor plates, black polycarbonate with white letters.  Microwave technology has an adjustable range of 2 inches to 24 inches.]

      - [Manual Operation:]

- NOTE:  Specify the power assist option for doors requiring ease of manual operation

        - [Operator shall provide power assist function to the doors to provide ease of manual operational forces.]

          - Manual push force to 15 lbf maximum.

- NOTE:  Consult SpecDesk for “push and go” operation option

        - [Operator shall be programmable to provide a “push and go” feature allowing door to open automatically if pulled or pushed open manually.]

- NOTE:  Consult SpecDesk for safety device recommendations – safety sensors are not required by ANSI/BHMA A156.19 for low-energy operators

- NOTE:  Retain the following if safety devices are required for the project – requires “safety sensor integration” option on power operator

      - [Safety Devices:]

        - Door Mounted Presence Sensor (DMPS):  Shall be the ASSA ABLOY door mounted infrared presence safety device (mounted at top of each door); adjustable to provide detection field sizes and functions required by ANSI/BHMA A156.10.

          - Unit to provide detection during the travel of the door.

          - Upon detection the sensor shall provide a signal to stop or reverse the door action.

        - Door Mounted Safety Sensor Devices:  Safety sensor devices shall be door mounted as specified.

- NOTE:  Select one of the following mounting options for door mounted safety sensor devices

          - [The door mounted safety sensor devices shall be mounted on both the swing (pull) side and the approach (push) side of the door (2 safety sensors per leaf), providing detection on sides of the door.]

          - [The door mounted safety sensor devices shall be mounted on the swing (pull) side of the door (1 safety sensor per leaf), providing detection on one side of the door only.]

          - [The door mounted safety sensor devices shall be mounted on the approach (push) side of the door (1 safety sensor per leaf), providing detection on one side of the door only.]

          - Power transfer from the door mounted safety sensor to operator shall be through an exposed door cord.

  - ALUMINUM FINISHES

- NOTE:  Consult SpecDesk for custom finish options

    - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

    - [Anodized Finish:]

      - [AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

      - [AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

      - [AAMA 611, Custom anodized to match architect’s sample.]

    - [Painted Finish:]

      - [Powder coat painted to match architect’s sample.]

      - [Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

    - [To match architects sample.]

- NOTE:  Delete following if MicroShield is not required.  Consult SpecDesk for availability of MicroShield with anodized and painted aluminum finishes

    - [MicroShieldTM antimicrobial silver-based ion, baked-on enamel finish on all exposed surfaces including door pulls, door extrusions, rails and header.]

      - Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew by the controlled release of silver ions that attack microbes and inhibit the growth on the treated surfaces.

      - Coating to be EPA registered resulting in a safe and non-toxic finish; chlorinated or synthetic chemical finishes will not be accepted.

- EXECUTION

  - EXAMINATION

    - Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance.

    - Examine roughing-in for electrical source power to verify actual locations of wiring connections.

    - Proceed only after such discrepancies or conflicts have been resolved.

  - INSTALLATION

    - Do not install damaged components.  Fit frame joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Install intensive care unit/critical care unit (ICU/CCU) entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

      - Install surface mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, carrier assemblies, tracks, operating brackets and guides level and true to location with anchorage for permanent support.

      - Where aluminum will contact dissimilar metals, concrete, or masonry, protect against galvanic action and corrosion.

    - Door Operators:  Connect door operators to electrical power distribution system as specified in Division 26 Sections.

    - Glazing:  Glaze intensive care unit/critical care unit (ICU/CCU) entrance door panels in accordance with the Glass Association of North America (GANA) Glazing Manual, published recommendations of glass product manufacturer, and published instructions of ICU/CCU entrance manufacturer.

    - Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to provide a weather tight installation.

      - Set thresholds, bottom guide and track systems and framing members in full bed of sealant.

      - Seal perimeter of framing members with sealant.

    - Signage:  Apply signage on both sides of each door and sidelite as required by  ANSI/BHMA A156.19 and manufacturers installation instructions.

  - ADJUSTING

    - Adjust alignment of entrances and hardware for smooth, safe operation with minimum air infiltration.

    - Adjust door operators and controls for smooth operation and in compliance with ANSI/BHMA A156.19.

    - Verify installation and alignment of all entrance gasketing as required for minimum air infiltration and compliance with specified standards.

  - FIELD QUALITY CONTROL

    - Before placing doors into operation, AAADM certified technician shall inspect and approve doors for compliance with ANSI/BHMA A156.19.  Certified technician shall be approved by manufacturer.

  - CLEANING AND PROTECTION

    - Clean adjacent surfaces soiled by door installation.

    - Clean glass and metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages to match original finish.

  - DEMONSTRATION

    - Engage a factory-authorized representative to train Owner's maintenance personnel to adjust, operate, and maintain safe operation of the door.

END OF SECTION