SECTION 08 42 43 – INTENSIVE CARE UNIT/CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

Edit this entire Section by revising, deleting, and/or inserting subparagraphs to meet Project specific requirements.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - This section includes the following types of intensive care unit/critical care unit (ICU/CCU) entrance doors:

          - Interior, single and bi-parting, power operated, sliding intensive care unit/critical care unit (ICU/CCU) entrance doors with sidelites.

        - Related Sections:

          - Division 7 Sections for caulking to the extent not specified in this section.

          - Division 8 Section “Door Hardware” for hardware to the extent not specified in this Section.

          - Division 8 Section Glazing for materials and installation requirements of glazing for intensive care unit/critical care unit (ICU/CCU) entrance doors.

          - Division 26 and 28 Sections for electrical connections including conduit and wiring for sliding door operators.

          - Division 26 and 28 Sections for access control systems and devices.

          - Division 26 and 28 Sections for smoke and fire detection systems.

      - REFERENCES

        - References:  Comply with the version year adopted by the Authority Having Jurisdiction.

          - ANSI A117.1 - Accessible and Usable Buildings and Facilities.

          - ICC/IBC - International Building Code.

          - NFPA 70 - National Electrical Code.

          - NFPA 101 - Life Safety Code.

        - American National Standards Institute (ANSI).

          - ANSI Z97.1 Standards for Safety Glazing Material Used in Buildings.

        - American Society for Testing and Materials (ASTM).

          - ASTM B221 Standard Specification for Aluminum and Aluminum Alloy Extruded Bars, Rods, Wire, Profiles and Tubes.

          - ASTM B209 Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate.

        - American Architectural Manufacturers Association (AAMA).

          - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

        - National Association of Architectural Metal Manufacturers (NAAMM).

          - Metal Finishes Manual for Architectural Metal Products.

        - International Code Council (ICC).manufacturer’s specified requirements.

          - IBC:  International Building Code Building Code.

          - CBC: California Building Code.

      - DEFINITIONS

        - Activation Device: Device that, when actuated, sends an electrical signal to the door operator to activate the operation of the door.

          - Knowing act:	Consciously initiating the opening of a power operated door using acceptable methods including wall mounted switches such as push plates and controlled access devices such as keypads, card readers and key switches.

        - Safety Device: A device that detects the presence of an object or person within a zone where contact could occur and provides a signal to stop the movement of the door.

      - PERFORMANCE REQUIREMENTS

        - General: Provide doors that have been designed and fabricated to comply with specified performance requirements, as demonstrated by testing manufacturer’s corresponding standard systems.

        - Intensive care unit/critical care unit (ICU/CCU) door equipment accommodates up to 220 pounds (100 kg) weight of doors.

        - Entrapment Force Requirements:

          - Power Operated Sliding Doors: Not more than 15 lbf (67 N) required to prevent a door from closing when the door travel speed is at a rate not faster than 1 foot per second.

          - Sliding doors provided with a breakaway device shall require no more than 50 lbf (222N) applied 1 inch (25 mm) from the leading edge of the lock stile for the breakout panel to open.

- NOTE:  Delete the following if MicroShield is not required

        - [MicroShieldTM antimicrobial silver-based ion finish on all exposed surfaces including door pulls, door extrusions, rails and header to comply with the manufacturer’s specified requirements.]

          - Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew.

      - SUBMITTALS

        - Comply with Division 01 - Submittal Procedures.

        - Product Data:  Manufacturer's product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes.

        - Shop Drawings:  Submit manufacturer’s shop drawings, including elevations, sections and details, indicating dimensions, materials, and fabrication of doors, frames, sidelites, hardware, finish, options and accessories.

        - Samples: Submit manufacturer’s samples of aluminum finish.

        - Informational Submittals:  Manufacturer's product information and applicable sustainability program credits that are available to contribute towards a LEED rated project certification.

          - Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each Product specified under this Section.

        - Operating and Maintenance Manuals:  Provide manufacturers operating and maintenance manuals for each item comprising the complete door opening installation in quantity as required in Division 01, Closeout Submittals.  The manual to include the name, address, and contact information of the manufacturers providing the hardware and their nearest service representatives.  The final copies delivered after completion of the installation test to include spare parts list.

        - Warranties and Maintenance:  Special warranties and maintenance agreements specified in this Section.

      - QUALITY ASSURANCE

        - Manufacturers Qualifications:  Engage qualified manufacturers with a minimum 10 years of documented experience in manufacturing of doors and equipment of similar to that indicated for this Project and that have a proven record of successful in-service performance.

        - Installer Qualifications:  Installers, trained by the primary product manufacturers, with a minimum 5 years documented experience installing and maintenance of units similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

        - Source Limitations for intensive care unit/critical care unit (ICU/CCU) entrances:  Obtain each type of door, frame, and operator specified in this Section from a single source, same manufacturer unless otherwise indicated.

        - Emergency Exit door requirements: Comply with requirements of authorities having jurisdiction for sliding entrance doors serving as a required means of egress.

      - PROJECT CONDITIONS

        - Field Measurements:	Verify actual dimensions of openings to receive intensive care unit/critical care unit (ICU/CCU) entrances by field measurements before fabrication and indicate on shop drawings.

      - COORDINATION

        - Coordinate sizes and locations of recesses in concrete floors for recessed tracks and thresholds if applicable. Concrete, reinforcement and formwork are specified in Division 03.

        - Electrical System Roughing-in: Coordinate layout and installation of automatic entrances with connections to power supplies and access control system as applicable.

      - WARRANTY

        - General Warranty:  Reference Division 01, General Requirements.  Special warranties specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

        - Intensive care unit/critical care unit (ICU/CCU) entrances shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

        - During the warranty period a factory-trained technician shall perform service and affect repairs.

        - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal business hours.

        - Manufacturer shall have in place a dispatch procedure that shall be available 24 hours a Day, 7 Days a week for emergency call back service.

- PRODUCTS

      - MANUFACTURER

        - Manufacturer:  ASSA ABLOY Entrance Systems, 1900 Airport Road, Monroe, NC 28110. Toll Free (877) SPEC-123.  Phone (704) 290-5520 Fax (704 ) 290- 5555 Website www.assaabloyentrance.com contact: specdesk.na.aaes@assaabloy.com

        - Substitutions:  Not Permitted.

      - INTENSIVE CARE UNIT/CRITICAL CARE UNIT (ICU/CCU) ENTRANCES

        - Model:  Besam VersaMaxTM Touchless ICU/CCU Sliding Door Package (Basis of Design):

          - Touchless, power operated, sliding aluminum door, frame, and sidelite.

        - ICU/CCU  Sliding Entrance Door Configuration:

- NOTE:  Select door configuration(s) as required for the project

          - [Single slide, full breakout, ICU/CCU door system.]

            - Configuration:  Single slide, two equal panel door unit with one operable leaf and one sidelite unit.

            - Minimum Clear Door Opening Width: [41-1/2 inches for 8’-0” unit width.] [44-1/2 inches for 8’-6” unit width.]

            - Breakaway Capability:  Interior sliding leaf and sidelite unit.

            - Mounting:  Overhead header installed between jambs.

          - [Single slide, full breakout, 3-panel ICU/CCU door system.]

            - Configuration:  Single slide, three equal panel door unit with one operable leaf and two sidelite units.

            - Breakaway Capability:  Interior sliding leaf and both sidelite units.

            - Mounting:  Overhead header installed between jambs.

          - [Single slide, fixed sidelite, ICU/CCU door system.]

            - Configuration:  Single slide, two equal panel door unit with one operable leaf and one fixed sidelite unit.

            - Minimum Clear Door Opening Width: [41-1/2 inches for 8’-0” unit width.] [44-1/2 inches for 8’-6” unit width.]

            - Emergency Breakaway Capability:  Exterior sliding leaf only.

            - Mounting:  Overhead header installed between jambs.

          - [Single slide, surface mounted, ICU/CCU door system.]

            - Configuration:  Single slide door unit and no sidelites.

            - Minimum Clear Door Opening Width: [41-1/2 inches for 8’-0” unit width.] [44-1/2 inches for 8’-6” unit width.]

            - Breakaway Capability:  Sliding leaf only.

            - Mounting:  Surface mounted header and guide track installed on face of wall.

          - [Bi-parting, full breakout, ICU/CCU door system.]

            - Configuration:  Bi-parting, four equal panel door unit with two operable leaves and two sidelite units.

            - Breakaway Capability:  Interior sliding leaves and sidelite units.

            - Mounting:  Overhead header installed between jambs.

          - [Bi-parting, fixed sidelite, ICU/CCU door system.]

            - Configuration:  Bi-parting, four equal panel door unit with two operable leaves and two fixed sidelite units.

            - Emergency Breakaway Capability:  Exterior sliding leaves only.

            - Mounting:  Overhead header installed between jambs.

          - [Bi-parting, surface mounted, ICU/CCU door system.]

            - Configuration:  Bi-parting, two panel door unit with two operable leaves and no sidelite units.

            - Breakaway Capability:  Sliding leaves only.

            - Mounting:  Surface mounted header and guide track installed on face of wall.

          - Dimensions:	Confirm door package dimensions as indicated on Architectural drawings.

      - ALUMINUM DOORS AND FRAMES

        - Doors and Frames:  Extruded Aluminum, Alloy 6063-T5.

          - Door panels shall have a minimum .125 inch (3.2 mm) structural wall thickness including adjoining horizontal members and perimeter frames where applicable.

          - Door Construction shall be by means of an integrated corner block with 3/8 inch diameter all-thread through bolt from each stile.

          - Glass Stops shall be .062 inch (15.8 mm) wall thickness and shall provide security function as a standard by means of a fixed non-removable exterior section with glazing to be performed from the interior only.  Glazing stops that allow for glass removal from the exterior shall not be deemed as equivalent.

- NOTE:  Beveled glass stops available only with 1/4" glazing

            - [Beveled glass stops.]

          - Bottom rails shall be provided with a concealed adjustable sweep gasket that is capable of withstanding exposure to 400o F for a minimum of 30 minutes.

          - Vertical Stiles shall be [narrow stile 2-1/8 inch (54 mm).]  [medium stile 4 inch (102 mm).]

          - Bottom Rails shall be [4 inch (102 mm).]  [7 inch (178 mm).]  [10 inch (254 mm).]

          - [Intermediate Muntin shall be [1-3/4 inch (45 mm).]  [4 inch (102 mm).]

        - Glass:  Glazing shall comply with ANSI Z97.1, thickness as indicated.

- NOTE:  Select glazing types as required for project.  Add “Locations” to each of the following if multiple thickness glazing is required

          - Door Panel and Sidelite Glazing:  [1/4” (6 mm)] tempered, unless otherwise specified. [Optional glazing: 5/8” (16 mm), 1” (25 mm), 1-1/4” (31 mm)]

          - Glazing Installation:  Dry glazing; wet glazing not allowed.

            - See Division 8 Section Glazing for requirements.

            - [All Glazing furnished “by others”.]

- NOTE:  Consult SpecDesk for integral blind information – glazing by Besam

          - [Integral Blinds:  Glass to have blinds installed between glass panes (1-1/4 inch (31 mm) glass only).]

        - Door Carriers:  Manufacturer’s standard carrier assembly that allows vertical adjustment.

          - Roller Wheels:  Two (2) steel roller wheel, 2-3/16 inch (55 mm) diameter, per active door leaf for operation over replaceable extruded nylon 6/6 track. Single journal with sealed oil impregnated bearings.

          - Two (2) Self-aligning anti-risers per leaf.

        - Framing Members:  Provide ICU/CCU entrances as complete assemblies.  Manufacturer’s standard extruded aluminum framing reinforced as required to support loads.

          - Vertical Jambs shall be 1-3/4 inches (44.5 mm) by 4-1/2 inches (114.3 mm).

        - Header:  Closed design extruded aluminum header unit extending full width of entrance unit to conceal door carrier assemblies, and roller track, complete with hinged access panel for service and adjustment.

          - Size:  8-1/2 inches (215.9 mm) wide by 4-3/4 inches (120.7 mm) high.

          - Hinge Point:  Continuous hinge at top of header allows for complete access for adjustments.

          - Design:  Manufacturer’s standard closed header.

        - [Anti-Static Option:  Fabricate ICU/CCU entrances to be internally grounded to reduce static shock.]

        - Hardware:  Provide manufacturer’s standard hardware as required for operation indicated.

          - Breakaway arms and bottom pivot assembly shall allow panels to breakout to 90 degrees.  Force to breakout slider panel adjustable to a maximum 50 lbf (222 N).

            - [Gas regulated damper to control movement of breakout panels.]

- NOTE:  Magnetic catches are optional, in lieu of the standard ball catch

            - [Besam Nurse Assist magnetic catch(s) to retain breakout door panel(s) in the closed position.]

- NOTE:  Optional positive latching for sliding ICU/CCU door system – latching hardware option for full breakout entrances includes the flush bolts

- NOTE:  The hardware required for the access control system does not replace the positive latching hardware

- NOTE:  Optional positive latching hardware is not available for bi-parting entrances

          - [Latching hardware shall be provided as indicated.]

            - Positive Latch: Mortise type self-latching hookbolt, BHMA A156.5, Grade 1, with lever handles on each side.

              - [Lever Style:  End of lever to have a return towards door face.]

              - Electrified strike to automatically release upon activation of sliding door operator.

              - Manual operated flush bolt to secure sidelite panel(s).

- NOTE:  Recessed pull/C-shaped  pull are provided standard on sliding ICU/CCU doors, not available with positive latching door hardware

          - [Door pulls shall be provided as indicated.]

            - [Manufacturer’s recessed pull installed on breakout side and surface-mounted, C-shaped pull installed on non-breakout side of active door leaves.  Door pull mounting shall not decrease clear opening width.]

- NOTE:  Optional C-shaped pull on both sides of sliding ICU/CCU door system

            - [Manufacturer’s surface-mounted, C-shaped, door pull installed on both sides of active door leaves.  Door pull mounting shall not decrease clear opening width.]

- NOTE:  Flush bolt option is always required when the VersaMax full breakout trackless option is specified with C-shaped pulls on both sides of the door

          - [Flush Bolts:  Manual operated flush bolt to secure sidelite panel(s).]

          - Power driven open/close operation shall be provided as indicated.

            - A power driven open/close operator activated by a touchless, knowing act type sensing device.

        - Guide Track/Threshold:  Manufacturer’s threshold as indicated.

- NOTE:  Track option 1 & 2 are available for full breakout when door system is installed between the jambs

- NOTE:  When specifying the VersaMax full breakout trackless option, flush bolts are always required when C-shaped pulls are to be on both sides of the door

          - [Trackless Design:  Floor mounted guide track and threshold not allowed.]

            - Breakout from a full open position only.

          - [Track:  1/2-inch (12.7 mm) high aluminum guide track floor mounted in front of the sidelight portion of the door assembly.]

            - [Surface mounted track.]  [Recessed mounted track.]

            - Guide track shall allow breakout from any position except when door is latched.

- NOTE:  Track option 3 is available only for fixed sidelite when door system is installed between the jambs

          - [Trackless Design:  Aluminum guide integrated into the bottom of the sidelight portion of the door assembly.]

            - Guide shall allow breakout from any position except when door is latched.

- NOTE:  Track option 4 is for a surface mounted door system

          - [Track:  Aluminum guide track mounted to the face of the wall.]

            - Wall mounted track with attached cover, to match the finish of the door assembly.

            - Guide track shall allow breakout from any position except when door is latched.

      - SLIDING DOOR OPERATOR

        - Door Operator and Controller:

          - Shall be a Besam electro-mechanical controlled unit utilizing a high-efficiency, energy efficient, DC motor requiring a maximum of 3 amp current draw.    System has capability to operate at full performance well beyond brown out and high voltage line conditions (85V – 265V) sensing changes and adjusting automatically.  Operator shall allow an adjustable hold open time of 0 to 60 seconds.

          - [Convenience Battery: Shall be concealed in header and capable of full operation with blackout conditions, including sensor capabilities for minimum of 100 cycles.]

        - Microprocessor Control Box:

          - Besam factory-adjusted configuration, with pre-set opening and closing speeds.

          - Selector switch to be interior jamb mounted and shall allow the following functions to be engaged when switch is turned to the appropriate setting.  Switch shall be a multi- position [keyed cylinder]  [rotary knob switch].

            - “Off”

            - “On”

            - “Hold Open” doors activated and held in the full open position.

      - ACTIVATION AND SAFETY CONTROL DEVICES

        - General:  Provide the types of activation and safety devices specified, for the condition of exposure and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.  Coordinate activation and safety devices with door operation and door operator mechanisms.

- NOTE:  The following is provided as the standard method of activation

        - Knowing Act Activation:

          - Sensor Plate:  Touchless, [jamb mounted]  [4-1/2 inch square wall mounted] activation senor plates, black polycarbonate with white letters.  Microwave technology has an adjustable range of 2 inches to 24 inches.

- NOTE:  The following Besam Header Mounted Presence Safety Sensor is provided as a standard feature for full breakout and fixed sidelite entrances

- NOTE:  The Besam Header Mounted Presence Safety Sensor is available as an option with surface mounted entrances for a redundant safety option

        - Safety Presence Sensors:

          - [Header Mounted Safety Sensor:  Shall be the Besam OA Presence Safety Sensor utilizing active infrared reflection technology to detect presence from a single housing mounted on each side of the header.]

- NOTE:  The following photoelectric safety beams are provided as a standard feature for the surface mounted entrance

- NOTE:  The photoelectric safety beams are provided as an option to the Besam Header Mounted Presence Safety Sensor for full breakout and fixed sidelite entrances

          - [Photoelectric Safety Beams:  Shall be two (2) Besam transmitter/receiver assemblies with infrared photoelectric beams on each side of the frame, to stop the door movement when the beam is broken.  Beams shall not be active when doors are fully closed.]

          - Breakout Beam:  Shall be a transmitter/receiver assembly with an infrared photoelectric beam, to stop the sliding door movement when the door is in the breakout position and breaks the photoelectric beam.

          - Presence detecting sensors to be field installed and adjusted.

- NOTE:  The following hardware is required if the entrance is to be connected to an access control system

- NOTE:  The following latching hardware is required in addition to positive latching hardware if positive latching is specified, but the positive latching hardware is not required for the access control system

- NOTE:  Card reader/keypad activation  is not available for bi-parting entrances

        - [Card Reader / Keypad Activation:]

          - Latching Hardware:  Provide latching hardware for connection to an access control system as indicated.

            - Positive Latch: Mortise type self-latching hookbolt, BHMA A156.5, Grade 1.

              - No lever handles are to be provided.

            - Electrified strike to automatically release the positive latch upon activation from access control system and allow the sliding function of the door panels.

- NOTE:  Fail safe operation is provided as a standard feature with card reader/keypad activation, fail secure operation is not available

              - Fail safe operation:  Electrified strike shall unlock the sliding function of the door panels upon loss of power or upon receiving a signal from the smoke detection system and/or fire detection system.

              - Electrified strike to be provided with the required power supply and sequencing relays for a complete operable system.

- NOTE:  Consult the SpecDesk for information on the VersaMax Management System

        - [Remote Activation:]

          - VersaMax Management System:  Remote activation system allowing remote activation by patient, nurse, smoke/fire detection system, and/or security system.

      - ALUMINUM FINISHES

- NOTE:  Consult SpecDesk for custom finish options

        - Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

        - [Anodized Finish:]

          - [AAMA 611, Clear, AA- M12C22A41, Class I, 0.018 mm.]

          - [AAMA 611, Dark Bronze, AA-M12C22A44, Class I, 0.018 mm.]

          - [AAMA 611, Custom anodized to match architect’s sample.]

        - [Painted Finish:]

          - [Powder coat painted to match architect’s sample.]

          - [Kynar finish, [2 coat]  [3 coat], to match architect’s sample.]

        - [To match architects sample.]

- NOTE:  Delete following if MicroShield is not required.  Consult SpecDesk for availability of MicroShield with anodized and painted aluminum finishes

        - [MicroShieldTM antimicrobial silver-based ion, baked-on enamel finish on all exposed surfaces including door pulls, door extrusions, rails and header.]

          - Antimicrobial finish must permanently suppress the growth of bacteria, algae, fungus, mold and mildew by the controlled release of silver ions that attack microbes and inhibit the growth on the treated surfaces.

          - Coating to be EPA registered resulting in a safe and non-toxic finish; chlorinated or synthetic chemical finishes will not be accepted.

- EXECUTION

      - EXAMINATION

        - Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, wall and floor construction, and other conditions affecting performance.

        - Examine roughing-in for electrical source power to verify actual locations of wiring connections.

        - Proceed only after such discrepancies or conflicts have been resolved.

      - INSTALLATION

        - Do not install damaged components.  Fit frame joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

        - Install intensive care unit/critical care unit (ICU/CCU) entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

          - Install surface mounted hardware using concealed fasteners to greatest extent possible.

          - Set headers, carrier assemblies, tracks, operating brackets and guides level and true to location with anchorage for permanent support.

          - Where aluminum will contact dissimilar metals, concrete, or masonry, protect against galvanic action and corrosion.

        - Door Operators:  Connect door operators to electrical power distribution system as specified in Division 26 Sections.

        - Glazing:  Glaze intensive care unit/critical care unit (ICU/CCU) entrance door panels in accordance with the Glass Association of North America (GANA) Glazing Manual, published recommendations of glass product manufacturer, and published instructions of intensive care unit/critical care unit (ICU/CCU) entrances manufacturer.

        - Sealants:  Comply with requirements specified in division 7 Section “Joint Sealants” to provide weather tight installation.

          - Set thresholds and framing members in full bed of sealant.

          - Seal perimeter of framing members with sealant.

        - Signage:  Apply signage on both sides of each door and sidelite as required by manufacturer.

      - FIELD QUALITY CONTROL

        - Manufacturers Field Services:

          - Manufacturer’s representative shall provide technical assistance and guidance for installation of doors.

      - ADJUSTING

        - Adjust doors and hardware for smooth, safe operation.

      - CLEANING AND PROTECTION

        - Clean adjacent surfaces soiled by door installation.

        - Clean glass and metal surfaces promptly after installation. Remove excess sealants, compounds, dirt and other substances. Repair damages finish to match original finish.

          - Comply with requirements in Division 08 Section Glazing for cleaning and maintaining glass.

END OF SECTION